Section Cover Page

Section 10 44 16 2008-05-01 Hand Held Fire Extinguishers

This Master Specification Section contains:

.1	This Cover Page

.2	Data Sheet - General

.3	Specification Section Text:

1.	General

1.1	Related Requirements

2.	Products

2.1	Hand Held Fire Extinguishers - Generally

2.2	Hand Held Fire Extinguishers

2.3	Fire Extinguisher Cabinet

3.	Execution

3.1	Installation

Applicable Standards

1.	CAN/ULC-S508-1990	Rated and Fire Testing of Fire Extinguishers and Class D Extinguishing Media

FIRE EXTINGUISHER

Following is a summary of commonly available hand held fire extinguishers, capacities and corresponding ULC ratings:

Fire Extinguisher Capacity and ULC Rating

Extinguisher Type	Capacity	ULC Rating

Multi-Purpose Dry Chemical	1.1 kg	1A5BC

(Pressure Type)	2.2 kg	2A10BC

4.5 kg	4A40BC

9.0 kg	10A80BC

Carbon Dioxide	2.2 kg	5BC

4.5 kg	5BC

6.8 kg	10BC

Note:  Exact capacity versus ULC rating will vary slightly among manufacturers.

END OF DATA SHEET

1.	General

1.1	RELATED REQUIREMENTS

.1	Mechanical General Requirements:	Section 20 00 13.

2.	Products

2.1	HAND HELD FIRE EXTINGUISHERS - GENERALLY

.1	Provide hand held fire extinguishers rated in accordance with CAN/ULC S508-1990, Extinguishers, fire, Rating and Fire Testing of Fire Extinguishers and bearing ULC label.

2.2	HAND HELD FIRE EXTINGUISHERS

SPEC NOTE:  Refer to Product Selection Data Sheet for a guide to specifying capacity and ULC ratings.

.1	Multi-Purpose Dry Chemical - Pressure Type:

.1	Description:  ammonium phosphate, powder type, heavy duty steel cylinder, baked enamel finish, squeeze grip handle with positive on/off valve, hose and nozzle, mounting brackets.

.2	Capacity:  [      ] kg.

.3	ULC Rating:  [           ].

.4	Classification:  Class A, B, and C fires.

.2	Carbon Dioxide:

.1	Description:  carbon dioxide charged heavy duty steel cylinder, baked enamel finish, positive on/off squeeze grip handle, impact resistance discharge horn, mounting bracket.

.2	Capacity:  [    ] kg.

.3	ULC Rating:  [     ] BC.

2.3	FIRE EXTINGUISHER CABINETS

.1	Fire Extinguisher Cabinet:  cabinet tub formed of minimum 1.6 mm steel.  Door and adjustable frame are fabricated of minimum 2.5 mm steel corrosion resistant treated, prime coated.

SPEC NOTE:  Where special cabinet finishes are required, coordinate requirements with Architect.  Modify this article to suit requirements.

.2	Semi-recessed with transparent canopy door.

SPEC NOTE:  Specify semi-recessed or fully recessed fire extinguisher cabinets.

OR

.2	Fully recessed type with approved latching device, prime coated, ULC listed, glass door.

3.	Execution

3.1	INSTALLATION

.1	Install fire extinguisher cabinet with top of cabinet 1.5 m above floor.

.2	Provide extinguishers of the type listed for the following areas.

.1	Electrical and telephone rooms:  carbon dioxide.

.2	Mechanical rooms:  multi-purpose dry chemical.

.3	Garbage and storage rooms:  multi-purpose dry chemical.

.4	Maintenance workshop:  multi-purpose dry chemical.

.5	Kitchen:  multi-purpose dry chemical.

.6	Suite Corridors:  multi—purpose dry chemical.

.7	[            ]

SPEC NOTE:  Edit list and add additional rooms to suit project requirements.

.3	Provide extinguishers where indicated on drawings.

.4	Where exact location is not indicated, mount in location as directed by the Minister.

END OF SECTION