Section Cover Page

Section 20 00 13 2010-12-01 Mechanical General Requirements

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	Intent

2.	Related Requirements

3.	Related Work Specified in Other Sections

4.	Utility Service Connections

5.	Materials

6.	Metric Conversion

7.	Cutting and Patching

8.	Shop Drawings

9.	Products Options and Substitutions

10.	Performance Verification of Installed Equipment

11.	Project Record Drawings

12.	Temporary Heat

13.	Equipment Protection and Clean-Up

14.	Temporary or Trial Usage

15.	Site Utility Services

16.	Electrical Motors

17.	Tenant Improvements

Do not under any circumstances specify ARI ratings for equipment.

1.	INTENT

.1	Provide complete, fully tested and operational mechanical systems to meet requirements described herein and in complete accord with applicable codes and ordinances.

.2	Contract documents of this Division and 300 series Drawings are diagrammatic and approximately to scale unless detailed otherwise.  They establish scope, material and installation quality and are not detailed installation instructions.

.3	Follow manufacturer's recommended installation details and procedures for equipment, supplemented by requirements of Contract Documents.

.4	Install equipment generally in locations and routes shown, close to building structure with minimum interference with other services or free space. Remove and replace improperly installed equipment to satisfaction of the Minister at no extra cost.

.5	Connect to equipment specified in other Sections and to equipment supplied and installed by other Contractors or by the Minister.  Uncrate equipment, move in place and install complete; start-up and test.

2.	RELATED REQUIREMENTS

.1	Submittals:	Division 01.

.2	Temporary Facilities:	Division 01.

.3	Temporary Heat:	Division 01.

.4	Contract Acceptance Procedures:	Division 01.

3.	RELATED WORK SPECIFIED IN OTHER SECTIONS

.1	Services connections:	Division 01.

.2	Painting, colour coding and identification

of mechanical work:	Section 09 91 30.

.3	Electric motor power characteristics:	Division 26.

.4	Earthwork General Requirements:	Section 31 20 10.

.5	Trench Excavating and Backfilling:	Section 31 23 38.

4.	UTILITY SERVICE CONNECTIONS

.1	Refer to Division 01 for requirements pertaining to utility service connections.

5.	MATERIALS

.1	Materials and equipment installed shall be new, full weight and of quality specified. Use same brand or manufacturer for each specific application.

.2	Statically and dynamically balance rotating equipment for minimum vibration and low operating noise level.

.3	Each major component of equipment shall bear manufacturer's name, address, catalog and serial number in a conspicuous place.

6.	METRIC CONVERSION

.1	All units in this division are expressed in SI units.

.2	Submit all shop drawings and maintenance manuals in SI units.

.3	On all submittals (shop drawings etc.) use the same SI units as stated in the specification.

7.	CUTTING AND PATCHING

.1	Provide holes and sleeves, cutting and fitting required for mechanical work.  Relocate improperly located holes and sleeves.

.2	Drill for expansion bolts, hanger rods, brackets, and supports.

.3	Obtain written approval from Minister before cutting or burning structural members.

.4	Provide openings and holes required in precast members for mechanical work.  Cast holes larger than 100 mm in diameter.  Field-cut smaller than 100 mm.

.5	Patch building where damaged from equipment installation, improperly located holes etc.  Use matching materials as specified in the respective section.

8.	SHOP DRAWINGS

.1	Comply with requirements of Division 01.

.2	Provide shop drawings as indicated.

.3	Identify materials and equipment by manufacturer, trade name and model number.  Include copies of applicable brochure or catalog material.  Do not assume applicable catalogues are available in the Minister's office. Maintenance and operating manuals are not suitable submittal material.

.4	Clearly mark submittal material using arrows, underlining or circling to show differences from specified, e.g. ratings, capacities and options being proposed.  Cross out non-applicable material.  Specifically note on the submittal specified features such as special tank linings, pumps seals materials or painting.

.5	Include dimensional and technical data sufficient to check if equipment meets requirements.  Include wiring, piping, and service connection data and motor sizes.

.6	Installed materials and equipment shall meet specified requirements regardless of whether or not shop drawings are reviewed by Minister.

.7	Shop drawings not requested will not be reviewed and processed by the Minister.

.8	Do not order equipment or material until Minister has reviewed and returned shop drawing.

9.	PRODUCTS OPTIONS AND SUBSTITUTIONS

.1	Refer to Division 01 for requirements pertaining to product options and substitutions.

10.	PERFORMANCE VERIFICATION OF INSTALLED EQUIPMENT

.1	Installed mechanical equipment whose performance is questioned by Minister, may be subject to performance verification as specified herein.

.2	When performance verification is requested, equipment shall be tested to determine compliance with specified performance requirements.

.3	Minister will determine by whom testing shall be carried out.  When requested, arrange for services of an independent testing agency.

.4	Testing procedures shall be approved by Minister.

.5	Maintain building comfort conditions when equipment is removed  from service for testing purposes.

.6	Promptly provide Minister with all test reports.

.7	Should test results reveal that originally installed equipment meets specified performance requirements, Minister will pay all costs resulting from performance verification procedure.

.8	Should test results reveal that equipment does not meet specified performance requirements, equipment will be rejected and the following shall apply:

.1	Remove rejected equipment.  Replace with equipment which meets requirements of Contract Documents including specified performance requirements.

.2	Replacement equipment will be subject to performance verification as well, using same testing procedures on originally installed equipment.

.3	Contractor shall pay all costs resulting from performance verification procedure.

11.	PROJECT RECORD DRAWINGS

.1	Submit record drawings identifying location of fire dampers, major control lines, EMCS sensors, access  doors, tagged valves and actual room names or numbers.

12.	TEMPORARY HEAT

.1	Do not use the permanent system for temporary heating purposes without written permission from the Minister.

.2	Thoroughly clean and overhaul permanent equipment used during the construction period, replace worn or damaged parts before final inspection.

.3	Use of permanent systems for temporary heat shall not modify terms of  warranty.

.4	Operate heating systems under conditions which ensure no temporary or permanent damage.  Operate fans at proper resistance with filters installed.  Change filters at regular intervals.  Operate with proper safety devices and controls installed and fully operational.  Operate systems only with treated water as specified.

.5	Where air systems are used during temporary heating, provide filter media on return and exhaust air outlets.  Clean duct systems which have become dirty.

.6	When permanent systems are used for temporary heat, provide alarm indicating system failure.  [Connect alarm to independent alarm company system].

.7	Where pumps are used for temporary heating, replace mechanical seals, regardless of condition, with new mechanical seals.

13.	EQUIPMENT PROTECTION AND CLEAN-UP

.1	Protect equipment and materials in storage on site during and after installation until final acceptance.  Leave factory covers in place.  Take special precautions to prevent entry of foreign material into working parts of piping and duct systems.

.2	Protect equipment with polyethylene covers and crates.

.3	Operate, drain and flush out bearings and refill with new change of oil, before final acceptance.

.4	Thoroughly clean piping, ducts and equipment of dirt, cuttings and other foreign substances.

.5	Protect bearings and shafts during installation.  Grease shafts and sheaves to prevent corrosion.  Supply and install necessary extended nipples for lubrication purposes.

.6	Ensure that existing equipment is carefully dismantled and not damaged or lost.  Do not reuse existing materials and equipment unless specifically indicated.

14.	TEMPORARY OR TRIAL USAGE

.1	Temporary or trial usage by the Minister of mechanical equipment supplied under contract shall not represent acceptance.

.2	Repair or replace permanent equipment used temporarily.

.3	Repair or otherwise rectify damage caused by defective materials or workmanship during temporary or trial usage.

15.	SITE UTILITY SERVICES

.1	Maintain liaison with the Minister to interrupt, re-route or connect to water, sewer, heating, or gas systems, with minimum interruption of services.

.2	Avoid thermal shock to heating system by co-ordination with the Minister during planning, construction and operation of temporary heating system.

.3	Return condensate to the heating plant.  Meter equipment is not required.

.4	Obtain approval from the Minister for thermal insulation work and automatic control equipment associated with temporary heating system.  Have temporary heating system approved by authority having jurisdiction.

16.	ELECTRICAL MOTORS

.1	Supply mechanical equipment complete with electrical motors.

.2	Provide motors to CEMA and CSA standards for hard, continuous service, designed to limit temperature rise to 40°C for open housing and 50°C for drip proof housing, and operate at 1200 or 1800 r/min unless otherwise specified.

.3	Motors shall have ball or roller type bearings.

.4	Provide grease lubrication fittings on motors with frame sizes 254T and larger.

.5	Refer to electrical specification for voltage, phase and cycle.

17.	TENANT IMPROVEMENTS

.1	Refer to Division 01 for requirements pertaining to Tenant Improvements portion of the project which will be performed under a unit price arrangement.

.2	Refer to Unit Price Schedule in Division 00 for Tenant Improvements mechanical work.

SPEC NOTE:  Include this article only on projects incorporating Tenant Improvements on a combined stipulated and unit price contract.

END OF SECTION