Section Cover Page

Section 20 05 25 Meters, Pressure 2008-05-01 Gauges and Thermometers

This Master Specification Section contains:

.1	This Cover Page

.2	Data Sheet - Reference Documents

.3	Specification Section Text:

1.	General

1.1	Related Sections

1.2	Shop Drawings and Product Data

2.	Products

2.1	Pressure Gauges

2.2	Thermometers

2.3	Pressure/Temperature Taps

2.4	Utility Meter

3.	Execution

3.1	Installation

3.2	Pressure/Temperature Taps

3.3	Gauge Schedule

Applicable Standards:

.1	ASTM B16-92	Free-Cutting Brass Rod, Bar and Shapes for Use in Screw Machines.

.2	CAN/CGSB 14.5-M88 	Thermometers, Bimetallic, Self-indicating, Commercial Type.

END OF DATA SHEET

1.	General

1.1	RELATED SECTIONS

.1	Mechanical General Requirements:	Section 20 00 13.

1.2	SHOP DRAWINGS AND PRODUCT DATA

.1	Comply with requirements of Section 20 00 13.

.2	Submit product data for each type of pressure gauge or thermometer indicating operating range, total range, accuracy, repeatability, size and style.

.3	Submit schedule of gauges and thermometers listing service, size, location, tag no., design operating parameters.

2.	Products

2.1	PRESSURE GAUGES

.1	Positive Pressure Gauge:

.1	Type:  pressure type.

.2	Accuracy:  accurate within 1%.

.3	Gauge Size:  110 mm diameter.

.4	Case Material:  steel, protected against corrosion and painted black.

.5	Crystal:  shatterproof glass.

.6	Mounting:  stem mounting at bottom of case.

.7	Bourdon Tube Material:  phosphor bronze.

.8	Dial Graduations:  kPa.

.9	Scale Range:

.1	Hydronic Systems:  [0-700 kPa] [0-1000 kPa]

.2	Domestic Water Systems:  [0-700 kPa] [0-1000 kPa].

.3	[                ].

.10	Stop:  bourdon tube and stop.

.11	Movement:  stainless steel or non-ferrous metal.

.12	Calibrator:  set screw.

.2	Compound Pressure Gauge:

.1	Type:  compound pressure.

.2	Accuracy:  accurate within ±1%.

.3	Gauge Size:  100 mm diameter.

.4	Case Material:  steel, protected against corrosion and painted black.

.5	Crystal:  shatterproof glass.

.6	Mounting:  stem mounting at bottom of case.

.7	Bourdon Tube Material:  phosphor bronze.

.8	Dial Graduations:  kPa.

.9	Scale Range:

.1	Hydronic Systems:

.1	Vacuum:  0-100 kPa.

.2	Pressure:  [0-700 kPa] [0-1000 kPa] [0-2000 kPa].

.2	Domestic Water Systems:

.1	Vacuum:  0-100 kPa.

.2	Pressure:  [0-700 kPa] [0-1000 kPa].

.3	[                ].

.10	Stop:  bourdon tube and stop.

.11	Movement:  stainless steel or non-ferrous metal.

.12	Calibrator:  set screw.

.3	Air System Static Pressure Gauge:

.1	Type:  pressure type.

.2	Accuracy:  within ±1%.

.3	Gauge Size:  110 mm diameter.

.4	Case Material:  aluminum alloy.

.5	Crystal:  shatterproof glass.

.6	Mounting:  stem mounting at back of case.

.7	Actuator:  diaphragm actuated.

.8	Dial Graduations:  Pa.

.9	Scale Range:  0-2000 Pa.

.10	Stop:  movement stop.

2.2	THERMOMETERS

.1	Stem Type Thermometer:

.1	Type:  any angle, adjustable.

.2	Class:  fixed calibration.

.3	Case Material:  steel, protected against corrosion and painted black.

.4	Crystal:  shatterproof glass.

.5	Case Length:  225 mm.

.6	Capillary Tube:  filled with red mercury.

.7	Graduations:  oC.

.8	Scale Range:

.1	Hot Water Heating:  0 - 110oC.

.2	Domestic Hot Water:  0-110oC.

.3	Domestic Cold Water:  0-50oC.

.4	[                  ].

.2	Dial Type Thermometer:  to CAN/CGSB 14.5-M88 and as follows:

.1	Type:  Type B - back connected.

.2	Class:  Class 1 - adjustable calibration.

.3	Stem Length:  300 mm.

.4	Dial Graduations:  oC.

.5	Dial Size:  75 mm diameter.

.6	Scale Range:

.1	Mixed Air Plenum:  -40oC to 40oC.

.2	Outside Air Plenum:  -40oC to 40oC.

.3	Other:  0oC to 100oC.

.3	Thermometer Wells:  to CAN/CGSB 14.5-M88 and as follows:

.1	Construction:  one piece brass construction.

.2	Diameter:  6 mm.

.3	Depth:  to suit thermometer stem.

2.3	PRESSURE/TEMPERATURE TAPS

.1	Fitting to allow a 3 mm O.D. plug-in gauge to measure temperature or pressure.

.1	Maximum pressure:  3450 kPa.

.2	Maximum temperature:  135oC.

.2	Fitting constructed of:

.1	13 mm NPT brass body with hex head screw cap.

.2	Two self-closing valves constructed of nordel.

.3	Test kit including the following:

.1	One 65 mm diameter compound pressure gauge with 3 mm O.D. plug-in stem.

.2	One 125 mm diameter temperature gauge with 3 mm O.D. plug-in stem, range 0-110oC.

.3	One 125 mm diameter temperature gauge with 3 mm O.D. plug-in stem, range 0-50oC.

2.4	UTILITY METER

.1	Meter of same type and manufacture as utility company's meter.

3.	Execution

3.1	INSTALLATION

.1	Provide one compound pressure gauge per pump.  Install taps on pump suction, pump discharge and before strainer.  Pipe to gauge with needle valve on each tap.

.2	For gauges on liquid service, provide tee in piping with bronze pulsation damper and needle valve.

3.2	PRESSURE/TEMPERATURE TAPS

.1	Install pressure/temperature taps into threaded pipe nipples welded to wall of pipe.  Locate fittings in accessible spaces.

.2	Provide one pressure/temperature taps test kit.

.3	Install pressure/temperature taps in the following locations:

.1	Both sides of two-way control valves.

.2	All lines to three-way control valves.

.3	Major heating and cooling coils:  at common inlet and at outlet of each coil.

.4	Heat exchanger:  at inlet and outlet.

.5	Reheat coils:  at inlet and outlet.

3.3	GAUGE SCHEDULE

.1	Provide pressure gauges, thermometers, pressure gauge taps and thermometer taps as indicated on the drawings and as specified in the following Schedule:

.1	Positive Pressure Gauges:

.1	Expansion tanks.

.2	Pressure tanks.

.3	Standpipe and sprinkler water supply connection.

.4	Pressure reducing valves.

.5	Domestic water supply to building.

.2	Compound Pressure Gauges:

.1	Pumps.

.3	Air System Static Pressure Gauges:

.1	Supply fan discharge.

.4	Filter Differential Pressure Gauges:

.1	Built-up filter banks.

.5	Stem Type Thermometers:

.1	Headers to central equipment.

.2	Coil banks at inlet and outlet.

.3	Heat exchangers at inlet and outlet.

.4	Boilers at inlet and outlet.

.5	Heating supply and return mains

.6	Domestic Hot water supply at each water heater

.6	Dial Type Thermometers:

.1	After coils or heating section in air system.

.2	Outside air intake.

.3	Return air plenum.

.4	Mixed air plenum.

.5	Supply air plenum

.7	Air System Static Pressure Taps:

.1	Inlet and discharge of supply and return fans.

.2	Inlet and discharge of coils.

.3	Inlet and discharge of mixing chambers.

END OF SECTION