Section Cover Page

Section 20 05 29 2008-05-01 Hangers and Supports

This Master Specification Section contains:

.1	This Cover Page

.2	Data Sheet - Reference Documents

.3	Specification Section Text:

1.	General

1.1	Reference Documents

1.2	Products Supplied But Not Installed Under This Section

1.3	General Requirements

1.4	Approvals

2.	Products

2.1	Pipe Hangers and Supports

2.2	Hanger Rods

2.3	Duct Hangers and Supports

2.4	Flashing

2.5	Sleeves

2.6	Finishes on Hanger Rods, Hangers and Supports

3.	Execution

3.1	Pipe Hangers and Supports

3.2	Low Velocity Duct Hangers and Supports

3.3	Equipment Bases and Supports

3.4	Flashing

3.5	Sleeves

Applicable Standards:

.1	ANSI/ASME B31.1-1995	Power Piping

.2	CAN/CGSB-1.40-M89	Primer, Structural Steel, Oil Alkyd Type

.3	NFPA 13-1996	Installation of Sprinkler Systems

END OF DATA SHEET

1.	General

1.1	REFERENCE DOCUMENTS

.1	Pipe supports shall meet the requirements of ANSI/ASME B31.1-1995, Power piping.

.2	Automatic sprinkler pipe supports shall meet the requirements of NFPA 13-1996, Standard for the Installation of Sprinkler Systems.

.3	Duct hangers shall follow the recommendations of the SMACNA Duct Manuals.

1.2	PRODUCTS SUPPLIED BUT NOT INSTALLED UNDER THIS SECTION

SPEC NOTE:  Delete this article if roof drains and plumbing vents are not specified.  Refer to applicable roofing specifications Section for installation of lead flashings and strip-in type plumbing flashing.

.1	Lead flashings for roof drains, for installation under Section [07 57 13] [       ].

.2	Strip-in type plumbing vent flashings, for installation under Section 07 57 15.

1.3	GENERAL REQUIREMENTS

.1	Provide hangers and supports to secure equipment in place, prevent vibration, maintain grade, provide for expansion and contraction and to accommodate insulation; provide insulation protection saddles.

.2	Install supports of strength and rigidity to suit loading without unduly stressing building.  Locate adjacent to equipment to prevent undue stresses in piping and equipment.

.3	Select hangers and supports for the service and in accordance with the manufacturer's recommended maximum loading.  Hangers shall have a safety factor of 5 to 1.

.4	Fasten hangers and supports to building structure.

.5	Provide and set sleeves required for equipment, including openings required for placing equipment.

.6	Dielectrically isolate dissimilar metals.

SPEC NOTE:  Refer to Basic Master Specification, Section 20 05 48 for Vibration Isolation Components and include as required.

1.4	APPROVALS

.1	Obtain approval from the Minister prior to installing supports for piping systems.

.2	Use of existing piping or equipment for hanger supports is not permitted.

.3	Use of perforated band iron, wire or chain as hangers is not permitted.

2.	Products

2.1	PIPE HANGERS AND SUPPORTS

.1	Hangers:  Pipe sizes 15 mm to 40 mm, adjustable wrought steel ring.

.2	Hangers:  Pipe sizes 50 mm to 100 mm and Cold Pipe Sizes 150 mm Over, adjustable wrought steel clevis.

.3	Multiple or Trapeze Hangers:  Steel channels with welded spacers and hanger rods.

.4	Wall Support:  Pipe Sizes to 80 mm, cast iron hook.

.5	Wall Support:  Pipe Sizes 100 mm and Over, welded steel bracket and wrought steel clamp.

.6	Vertical Support:  Steel riser clamp.

.7	Floor Support:  Pipe sizes to 100 mm Cold Pipe sizes, cast iron adjustable pipe saddle with locknut nipple and floor flange.

.9	Design hangers so they cannot become disengaged by movements of supported pipe.

.10	Provide copper plated hangers and supports for copper piping or provide sheet lead packing between hanger or support and piping.

2.2	HANGER RODS

.1	Provide steel hanger rods, threaded both ends, threaded one end, or continuous threaded.

2.3	DUCT HANGERS AND SUPPORTS

.1	Hangers:  Galvanized steel band iron or rolled angle and 10 mm rods.

.2	Wall Supports:  Galvanized steel band iron or fabricated angle bracket.

.3	Vertical Support at Floor:  Rolled angle.

2.4	FLASHING

.1	Steel Flashing:  0.55 mm galvanized steel.

.2	Lead Flashing:  sheet lead, as follows:

.1	For waterproofing:  25 kg/m2

.2	For Soundproofing:  5 kg/m2.

.3	Lead Sheet Size:

.1	Roof Drains:  minimum 810 mm x 810 mm.

.2	Roof Plumbing Vents:  as required to provide base flashing overlap to ARCA detail.

.3	Floor Drains:  minimum 920 mm x 920 mm and as specified.

.4	Other Locations:  as specified.

.4	Caps:  Steel, 0.7 mm thickness minimum, 1.6 mm thickness at  fire resistance structures.

2.5	SLEEVES

.1	Pipes through Floors:  Form with 1.2 mm galvanized steel.

.2	Pipes through Beams, Walls, Fire Proofing, Footings, Potentially Wet Floor:  Form with steel pipe or 1.2 mm thickness galvanized steel.

.3	Round Ducts:  Form sleeves with galvanized steel.

.4	Rectangular Ducts:  Form sleeves with galvanized steel or wood.

.5	Size large enough to allow for expansion with continuous insulation.

2.6	FINISHES ON HANGER RODS, HANGERS AND SUPPORTS

.1	All steel hanger rods, hangers and supports shall be galvanized or factory primed with alkyd red oxide primer to CAN/CGSB-1.40-M89.

3.	Execution

3.1	PIPE HANGERS AND SUPPORTS

.1	Support horizontal steel and copper piping as follows:

Nominal Pipe	Distance Between	Hanger Rod

Size	Supports	Diameter

15 mm	1.8 m	10 mm

20 mm to 40 mm	1.8 m	10 mm

50 mm & 65 mm	  3 m	10 mm

80 mm & 100 mm	3.6 m	16 mm

150 mm to 300 mm	4.3 m	22 mm

.2	Install hangers to provide minimum 12 mm clear space between finished covering and adjacent work.

.3	Place a hanger within 300 mm of each horizontal elbow.

.4	Use hangers which are vertically adjustable 40 mm minimum after piping is erected.

.5	Support horizontal soil pipe near each hub with 1.5 m maximum spacing between hangers.

.6	Support vertical piping at every other floor.  Support vertical soil pipe at each floor at hub.

.7	Where several pipes can be installed in parallel and at same elevation, provide multiple or trapeze hangers.

.8	Where practical, support riser piping independently of connected horizontal piping.

3.2	LOW VELOCITY DUCT HANGERS AND SUPPORTS

.1	Hanger Minimum Sizes:

.1	Up to 750 mm wide:  25 x 1.6 mm at 3 m spacing.

.2	790 to 1200 mm wide:  40 x 1.6 mm at 3 m spacing.

.2	Horizontal Duct on Wall Supports Minimum Sizes:

.1	Up to 450 mm wide:  40 x 1.6 mm or 25 x 25 x 3 mm at 2.4 m spacing.

.2	480 x 1000 mm wide:  40 x 40 x 3 mm at 1.2 m spacing.

.3	Vertical Duct on Wall Supports Minimum Sizes at 3.65 m spacing:

.1	Up to 610 mm wide:  40 x 1.6 mm.

.2	640 to 900 mm wide:  25 x 25 x 3 mm.

.4	Vertical Duct Floor Supports Minimum Sizes, riveted or screwed to ducts:

.1	Up to 1520 mm wide:  40 x 40 x 3 mm.

3.3	EQUIPMENT BASES AND SUPPORTS

.1	Provide for major equipment, reinforced concrete housekeeping bases poured directly on structural floor slab 100 mm thick minimum, extended 100 mm minimum beyond machinery bedplates.  Provide templates, anchor bolts and accessories required for mounting and anchoring equipment.

.2	Construct supports of structural steel members or steel pipe and fittings.  Brace and fasten with flanges bolted to structure.

.3	Rigidly anchor ducts and pipes immediately after vibration connections to equipment.

.4	Where fuel burning appliances are installed on combustible floors provide approved non-combustible bases.

3.4	FLASHING

.1	Flash and counterflash where mechanical equipment passes through weather or waterproofed walls, floors, and roofs.

.2	Flash vent and soil pipes projecting 75 mm minimum above roof membrane with lead worked 25 mm minimum into hub, 200 mm minimum clear on sides with minimum 600 x 600 mm sheet size.  For pipes through outside walls turn flange back into wall and caulk.

.3	Flash floor drains over finished areas with lead 250 mm clear on sides with minimum 920 x 920 mm sheet size.  Fasten flashing to drain clamp device.

.4	Provide curbs for mechanical roof installations minimum 200 mm high.

.5	Attach counterflashings to mechanical equipment and lap base flashings on roof curbs.

.6	Flatten and soldered double seam joints in counterflashing.  Provide adjustable storm collars to draw tight to pipe with bolts.  Caulk around the top edge.  Use storm collars above all roof jacks.

.7	Screw vertical flange section of roof jacks to face of curb.

.8	Provide lead flashing around ducts and pipes passing from equipment rooms, installed according to manufacturer's data for sound control.

3.5	SLEEVES

.1	Set sleeves in position in advance of concrete work.  Provide suitable reinforcing around sleeves.

.2	Extend sleeves through potentially wet floors 25 mm above finished floor level.  Caulk sleeves full depth and provide floor plate.

.3	Where piping or ductwork passes through floor, ceiling or wall, close off space between pipe or duct and construction with non-combustible insulation.  Provide tight fitting metal caps on both sides and caulk.

.4	Install chrome plated escutcheons where piping passes through finished surfaces.

END OF SECTION