Section Cover Page

Section 20 40 38 2010-12-01 Steam Specialties

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Quality Assurance

1.2	Submittals

2.	Products

2.1	Thermostatic Steam Traps

2.2	Float and Thermostatic Steam Traps

2.3	Bucket Steam Traps

2.4	Steam Air Vents

2.5	Steam Pressure Reducing Station

3.	Execution

3.1	Steam Trap Application

3.2	Steam Trap Sizing

3.3	Low Pressure Trap Assemblies

3.4	High Pressure Trap Assemblies

3.5	Steam Pressure Reducing Station

3.6	Relief Valves

1.	General

1.1	QUALITY ASSURANCE

.1	Low pressure steam is steam at 100 kPa or less.

.2	Comply with Provincial Regulations and have CSA approval.

1.2	SUBMITTALS

.1	Provide shop drawings and schedules for review where requested by the Minister.

2.	Products

2.1	THERMOSTATIC STEAM TRAPS

.1	Provide balanced pressure thermostatic type with semi-steel or cast brass body, bolted top, renewable stainless steel valve head and seat.

.2	Fabricate thermostatic element of bronze or monel metal.

2.2	FLOAT AND THERMOSTATIC STEAM TRAPS

.1	Provide fully modulating type suitable for continuous operation with semi-steel body and cover.

.2	Construct float, air vents, head, seat and valve mechanism of stainless steel.

2.3	BUCKET STEAM TRAPS

.1	Provide inverted bucket type suitable for intermittent operation with semi-steel body and cover.

.2	Construct bucket, seat, head, operating mechanism and strainer of stainless steel.

2.4	STEAM AIR VENTS

.1	Provide automatic steam air vents of the thermostatic balanced pressure type, with brass or semi-steel body, renewable stainless steel head and seat.

.2	Fabricate thermostatic liquid filled bellows of phosphor bronze.

2.5	STEAM PRESSURE REDUCING STATION

.1	Provide steam pressure reducing stations complete with pressure reducing valve[s], valved bypass, strainer and pressure gauge on upstream side, relief valve and pressure gauge on downstream side.

.2	Pressure reducing valve[s] shall have diaphragm, bronze body, balanced design, stainless steel trim and pilot operator.

3.	Execution

3.1	STEAM TRAP APPLICATION

.1	Install thermostatic steam traps to drain condensate from steam radiation units, convectors and other similar terminal heating units.

.2	Install float and thermostatic steam traps to drain condensate from unit heaters, convertors, heating coils, steam separators, flash tanks, steam jacketed equipment and direct steam injected equipment.

.3	Install inverted bucket steam traps to drain condensate from steam main headers and branch lines.

3.2	STEAM TRAP SIZING

.1	Size steam traps to handle a minimum of 2 times the maximum condensate load of the apparatus served.

.2	Traps used for dripping steam mains and branches shall be minimum 20 mm size.

3.3	LOW PRESSURE TRAP ASSEMBLIES

.1	Install trap with union or flanged connection at both ends.

.2	Provide gate valve and strainer at inlet, gate valve [and check valve] at discharge.

.3	Provide minimum 250 mm long dirt pocket of same pipe size as  apparatus return connection.

.4	Do not use thermostatic elements in traps until system has been operated and dirt pockets cleared of sediment and scale. Provide temporary covers for use prior to this time.

3.4	HIGH PRESSURE TRAP ASSEMBLIES

.1	Install trap with union or flanged connection at both ends.

.2	Provide gate valve and strainer at inlet, gate valve and check valve at discharge.

.3	Provide minimum 250 mm long dirt pocket of same pipe size as apparatus return connection.

.4	Do not use thermostatic elements in traps until system has been operated and dirt pockets cleared of sediment and scale. Provide temporary covers for use prior to this time.

3.5	STEAM PRESSURE REDUCING STATION

.1	Pressure reduction shall be one or two stages as required to produce flat reduced pressure curve for all ranges of capacity.

.2	Pilot operator control line shall connect downstream far enough to ensure true pressure.

.3	Rate relief valves for the station upstream steam pressure. Size for full installed capacity of reducing station. Set valve to relieve at not more than 20% above reduced pressure.

3.6	RELIEF VALVES

.1	Terminate vent lines from relief valves outdoors. Provide drip pan elbow with drain connection [to nearest floor drain].

.2	When several relief valve vents connect to one vent header, the header cross sectional area shall equal the sum of individual vent outlet area.

END OF SECTION