Section Cover Page

Section 21 13 10 2008-05-01 Sprinkler Equipment

Use this section to specify small sprinkler systems connected to the domestic water system serving individual rooms such as garbage and residents' storage areas.

This Master Specification Section contains:

.1	This Cover Page

.2	Data Sheet - Reference Documents

.3	Specification Section Text:

1.	General

1.1	General Requirements

1.2	Quality Assurance

2.	Products

2.1	Sprinkler Heads

3.	Execution

3.1	Installation

Applicable Standards

.1	NFPA13-1996	Installation of Sprinkler Systems

END OF DATA SHEET

1.	General

1.1	GENERAL REQUIREMENTS

.1	Provide complete sprinkler system as required by local Codes and as indicated on drawings.  Size of sprinkler system is based on ordinary hazard occupancy.

.2	Provide sprinklers for areas [as indicated on drawings,] [in residence storage area], including specialized rooms.

1.2	QUALITY ASSURANCE

.1	Sprinkler equipment and installation shall be reviewed and approved by local Fire Commissioner.

.2	Equipment and installation shall meet the requirements of NFPA 13-1996 - Standard for the Installation of Sprinkler Systems.

2.	Products

2.1	SPRINKLER HEADS

.1	Temperature rating on fusible links shall suit specific hazard area with minimum safety margin of 10°C.

.2	Provide standard pendant type with chrome plated finish and escutcheon in suspended ceilings.

.3	Provide standard upright type with brass  finish.  For sidewall application in exposed areas.

.4	Provide sidewall type with chrome plated finish and escutcheon in sidewall application.

3.	Execution

3.1	INSTALLATION

.1	Protect sprinkler heads against mechanical injury with standard guards where necessary.

.2	Provide 25 mm diameter nipple and 25 x 15 mm reducing fitting for each upright head.

.3	Provide approved assembly, consisting of gate valves on both sides of double check valves, at sprinkler system take-off from water supply.

END OF SECTION