Section Cover Page

Section 23 08 83 Balancing and Adjusting of 2021-03-31 Mechanical Equipment and Systems

Use this Section to specify all balancing and adjusting of mechanical equipment and systems.  Do not specify these requirements in individual technical sections; include cross-references to this Section 23 08 83 only.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Requirements

1.3	Testing/Adjusting/Balancing Report Data

2.	Products

Not Used

3.	Execution

3.1	Balancing and Adjusting Preparation

3.2	General Procedures

3.3	Fire Damper/Fire Stop Flap Verification

3.4	Airflow Measuring Stations

3.5	Air System Procedure

3.6	Miscellaneous Air Handling Devices

3.7	Combustion Air

3.8	Acoustic Measurements

3.9	Balancing of Hydronic Systems

3.10	Balancing and Adjusting of [Fire Pump] [Pressure Booster Pumps]

3.11	Balancing and Adjusting of Domestic Water Systems

3.12	Balancing and Adjusting of Emergency Generator Systems - Air Side

3.13	Balancing Report

1.	General

1.1	INTENT

.1	Test, adjust and balance mechanical equipment and systems so that entire system produces the results for which it was designed.

.2	Air and water balancing performed by the same firm.

1.2	RELATED requirements

.1	Contractor Start-Up Report Forms:	Division 01.

.2	Mechanical Operation and Maintenance Data:	Section 20 01 05.

.3	Mechanical Operation and Maintenance Manual:	Section 20 01 06.

.4	General Mechanical Starting and Testing Requirements:	Section 23 08 13.

.5	Mechanical Equipment Starting and Testing:	Section 23 08 23.

.6	Mechanical Systems Starting and Testing:	Section 23 08 33.

.7	EMCS Start-up and Testing:	Section 23 08 95.

1.3	TESTING/ADJUSTING/BALANCING REPORT DATA

.1	Organize balancing data in accordance with AABC - Associated Air Balancing Council, report format.  Report data in SI units.

.2	Air Systems:  Include both specified and measured data.

.1	Air Handling Equipment:

.1	Maximum air flow volume.

.2	Fan total pressure.

.3	Motor volts, amps and power.

.4	Minimum outside air volume.

.5	Fan rotational speed.

.6	Fan Power, calculate fan efficiency.

.7	Inlet and outlet dry and wet bulb temperatures.

.8	Equipment static pressure profile.

.2	Duct Air Quantities - Mains and Branches:

.1	Duct size.

.2	Number of pressure/velocity readings per traverse.

.3	Sum of velocity measurements.

.4	Average velocity.

.5	Duct air flow volume.

.6	Barometric pressure and duct air temperature.

.3	Air Outlets:

.1	Outlet location and designation.

.2	Manufacturers catalogue identification and type.

.3	Air outlet flow factors. Use 1.0 when flowhood is used.

.4	Air flow volumes.

.5	Deflector vane or diffuser cone settings.

.4	Emergency Generator:

.1	Air flow volume. Air flow volume includes cooling plus combustion air.

.2	Static pressure profile.

.3	Hydronic Systems:  Include both specified and measured data.

.1	Pumps:

.1	Discharge and suction pressures, at design flow and no flow.

.2	Fluid flow rate. Calculate from pump curves if metering not provided.

.3	Motor volts, amps, power.

.2	Heating Equipment:

.1	Equipment type, location and designation.

.2	Fluid used. Identify fluid used; water, % water/glycol mixes, steam, etc.

.3	Fluid flow rate.

.4	Fluid Specific Heat, at mean temperature.

.5	Fluid Specific Gravity, at mean temperature.

.6	[Fluid entering and leaving temperatures and pressures]. [Steam pressure, and condensate temperature].

.7	Heat transfer rate.

.3	Heat Exchanger:

.1	Heating fluid used. Identify fluid used; water, % water/glycol mixes, steam, etc.).

.2	Heating fluid flow rate.

.3	Heating fluid Specific Heat, at mean temperature.

.4	Heating fluid Specific Gravity, at mean temperature.

.5	[Heating fluid entering and leaving temperatures and pressures]. [Steam pressure, and condensate temperature].

.6	Primary side heat transfer rate.

.7	Heated fluid used. Identify fluid used; water, % water/glycol mixes, etc.).

.8	Heated fluid flow rate.

.9	Heated fluid Specific Heat, at mean temperature.

.10	Heated fluid Specific Gravity, at mean temperature.

.11	Heated fluid entering and leaving temperatures and pressures.

.12	Secondary side heat transfer rate.

.4	Air Heating and Cooling Coils:

.1	Coil type and identification, location and designation.

.2	Entering and leaving air dry and wet bulb temperatures.

.3	Air static pressure drop.

.4	Air flow volume.

.5	Barometric pressure.

.6	Air side heat transfer rate.

.7	Fluid used. Identify fluid used; water, % water/glycol mixes, steam, etc.

.8	Fluid flow rate.

.9	Fluid Specific Heat, at mean temperature.

.10	Fluid Specific Gravity, at mean temperature.

.11	[Fluid entering and leaving temperatures and pressures]. [Steam pressure, and condensate temperature].

.12	Fluid side heat transfer rate.

.5	Unit and Cabinet Heater:

.1	Start unit and check for noise or vibration.

.2	Check unit performance for each fan speed:

.1	Air flow and temperature rise.

.2	Water temperature drop.

.6	Water Chiller:

.1	Fluid used. Identify fluid used; water, % water/glycol mixes, etc.

.2	Fluid flow rate.

.3	Fluid Specific Heat, at mean temperature.

.4	Fluid Specific Gravity, at mean temperature.

.5	Fluid entering and leaving temperatures and pressures.

.6	Heat transfer rate.

.7	Chiller motor volts, amps and power.

.7	Cooling Tower:

.1	Condenser water flow rate.

.2	Condenser water temperature entering and leaving.

.3	Entering air dry and wet bulb temperature.

.4	Make-up water flow and entering temperature.

.5	Heat rejection at tower.

.6	Fan motor volts, amps and power.

.4	Sound Pressure Level Data:

.1	Overall A-weighted Sound Pressure Level readings.

.2	For outdoor equipment or community noise measurements provide a diagram or description of relationship of sound source to measuring instrument.

2.	Products

Not Used

3.	Execution

3.1	BALANCING AND ADJUSTING PREPARATION

.1	Perform testing, adjusting and balancing work after equipment and systems starting procedures have been properly completed in accordance with Sections 23 08 23 and 23 08 33.

.2	Perform balancing during heating and cooling season of first year of operation, and at times when directed by Province, to ensure proper settings of controls under both summer and winter peak load conditions.

.3	Vary load to verify operation of system under partial load conditions. Test start-up, shut-down, emergency conditions, safety controls operation and automatic and manual resets and interlocks.

.4	Perform work using measuring instrumentation conforming to requirements specified in Section 23 08 13.

3.2	GENERAL PROCEDURES

.1	Perform balancing to following accuracy:

.1	Air - terminal outlets	± 10%

.2	Air - central equipment	±  5%

.3	Hydronic - terminal outlets	± 10%

.4	Hydronic - pumps and central equipment	±  5%

.2	Permanently mark settings on splitters, valves, dampers or other adjustment devices.

.3	Subsequent to correcting work, take measurements to verify balance has not been disrupted or that any such disruption has been rectified.

.4	As a prerequisite to the Province's acceptance of balance report demonstrate random points in balance selected by the Province. The Province will witness these checks.

3.3	FIRE DAMPER/FIRE STOP FLAP VERIFICATION

.1	Visually inspect and document all fire dampers/fire stop flaps to verify that:

.1	Installation is straight and level.

.2	Wall angles are properly installed.

.3	Duct has break away connection.

.4	Fire stopping material, where used, is properly installed.

.5	Access is adequate.

.6 	Adequate clearance exists between sleeve and wall.

.7	ULC label is visible.

.8	Blades are out of air stream.

.9	Temperature rating of linkages are correct.

.2	Inspect and clean all fire damper blades and tracks prior to function test.

.3	Function test each damper, by detaching fusible link chain. Verify that damper blade drops properly and is tightly sealed within frame. Reset each damper.

.4	If fire damper does not close properly, repair installation and retest.

.5	All fire damper tests shall be witnessed by two parties, certified by Contractor and endorsed by testing personnel.

.6	Write to authority having jurisdiction prior to testing dampers.  Invite authority to witness tests as required.

3.4	AIRFLOW MEASURING STATIONS

.1	Measure air flow by duct traverse at five different air volumes equally spaced between design minimum and maximum for each station.

.2	Use EMCS trend logs to record air volume flow during time that each duct traverse is performed. Average trend log readings over this time period.

.3	Compare duct traverse and averaged trend log readings for each of the five air volume measurements taken. Calculate calibration correction equation.

.4	Document each calibration on Province approved Contractor Start-up Program “Flow Measuring Station Calibration” sheets.

3.5	AIR SYSTEM PROCEDURE

.1	Perform testing, adjusting and balancing only after all suspended ceilings and partitions are complete, with doors and windows in place and closed.

.2	Adopt following procedures for central systems:

.1	Test drop and reset all fire dampers.

.2	Verify that dampers and volume control devices are in fully open position.

.3	Initially balance central plant to ± 10% air flow.

.4	Calibrate air flow measuring stations.

.5	Balance mains and branches to ± 10% air flow.

.6	Recheck central plant.

.7	Balance all terminal air outlets to ± 10%.

.8	Rebalance central plant to ± 5%.

.9	Recheck all air outlets.

.10	Measure performance of coils and humidifier.

.11	Measure air pressure change across each component of central plant.

.12	Take sound pressure level readings.

.3	Take air flow measurements in ducts by "Pitot Tube" traverse of entire cross sectional area.  Take the number of readings as set out in ASHRAE Fundamentals Chapter on "Measurement and Instruments". If readings are inconsistent across duct, relocate by two duct diameters / widths and redo traverse.

.4	Following precedence applies to air flow measuring devices and methodology:

.1	Pitot tube traverses in straight sections of duct have precedence over anemometer or velometer traverses of filters, coils, ducts, etc.

.2	Micromanometer flowhood measurements at air outlets have precedence over anemometer or velometer readings at air outlets.

.3	A pitot tube traverse in a straight duct section at inlet to a variable volume box has precedence over a box air flow sensor reading.

.4	Variable volume box air flow sensor may be used to set up box maximum and minimum air volumes but, unless otherwise agreed with the Province, the sum of micromanometer flowhood readings at all air outlets has precedence over a box flow sensor reading.

.5	Use volume control devices at air outlets to regulate air quantities only to extent that adjustments do not create objectionable air motion or noise. Effect volume control primarily by duct internal devices such as dampers and splitters.

.6	Vary total system air quantities by adjustment of fan speeds.  Vary branch air quantities by damper regulation.

.7	Balance air systems at design minimum supply air temperature.

.8	When balancing constant volume systems:

.1	Rough balance furthest outlet and then balance sequentially back to source,

.2	Fine balance furthest outlet back to source.

.9	When balancing variable air volume systems:

.1	Check factory settings and reset each box maximum and minimum air volumes as necessary.

.2	Measure inlet static pressure to box at maximum volume.

.3	Individually set each box to maximum, rough balance furthest outlet and then balance sequentially back to box.

.4	Fine balance from furthest outlet back to box.

.5	Check damper stroke over box range, minimum to maximum.

.6	With all boxes at minimum volume progressively open boxes in a clockwise direction until maximum design air volume is achieved, or until branch static pressure can no longer be maintained. Check that each opened box is delivering specified maximum volume by checking and recording if the inlet static pressure is adequate to operate the box at maximum volume.  Record airflow measuring station volume.  Determine minimum duct static pressure at sensor that will provide adequate inlet pressure at every box.

.7	With all boxes at maximum volume, progressively close boxes in a clockwise direction until branch static pressure is achieved. Check that each opened box is delivering specified maximum volume. Record system volume. Determine minimum duct static pressure at sensor that will provide adequate inlet pressure at every box.

.10	Upon completion of balancing, recheck and record data from central Air Handling Unit (refer to Section 23 08 23) including following:

.1	Motor data.

.2	Coil, filter, humidifier data.

.3	Static pressure profile across all components.

.4	Damper controls.

.11	Final balanced condition of each area shall include testing and adjusting of pressure conditions.  Test, adjust and record building and zone pressurization levels.  For variable volume systems check pressurization throughout full range of fan delivery for both heating and cooling conditions.  For multi-story buildings test pressure conditions at ground, intermediate and upper levels.  Check front doors, exits and elevator shafts for air flow so that exterior conditions do not cause excessive or abnormal pressures.  Document abnormal building leakage conditions noted.

.12	Complete balancing to achieve positive building pressure unless otherwise instructed.

.13	[Complete balancing on smoke control systems in all modes of operation.]

3.6	MISCELLANEOUS AIR HANDLING DEVICES

.1	Motorized Smoke and Gravity/Barometric Dampers:

.1	Review installation to ensure:

.1	No cracks around damper frame.

.2	Blades close and seals engage completely.

.3	Damper strokes fully open to fully closed with no binding of blades at any part of stroke.

.4	Suitable access and identification.

.2	Air Outlets:

.1	Review installation to ensure:

.1	Air outlet is clean.

.2	Air outlet is located as shown on drawings.

.3	Balancing Dampers:

.1	Check installation to ensure:

.1	Damper can open and close fully.

.2	Access is clearly marked.

.3	Damper is not located in a turbulent air stream.

3.7	COMBUSTION AIR

.1	With all heating appliances, within the boiler room, operating on high fire, measure:

.1	Combustion air volume entering boiler room from outside.

.2	Differential pressure to:

.1	Outside

.2	Adjacent areas of the building.

.2	With all heating appliances on high fire, check each natural draft appliance diverter for any back draft.

3.8	ACOUSTIC MEASUREMENTS

.1	Acoustic Measurement Procedure:

.1	Use Sound Level Meter as specified in Section 23 08 13.

.2	Calibrate microphone and sound level meter before use.

.3	Hold Sound Level Meter in front of body of observer and as far away as is practicable or attach instrument to a tripod stand.

.4	Height of measuring microphone from floor shall be 1200 mm ±50 mm unless otherwise noted.

.5	Measurement locations shall be minimum of one metre away from any large vertical or horizontal surface, ie. walls, columns, floors.

.6	Take measurements with meter on “SLOW” response or follow manufacturer’s instructions for Leq “equivalent energy level” averaging.

.7	Do not take readings until noise created by extraneous equipment, people or other sources, which would interfere with specific acoustic measurements, have ceased.

.2	HVAC Noise Inside Building:

.1	The objective is to measure Sound Pressure Level within each occupied room created by entire HVAC system and to evaluate these in terms of the recommended maximum background noise levels for each type or area.  Investigate areas found to be in excess of recommended maximum levels and take corrective action.

.2	Follow testing procedures specified under "Acoustic Measurement Procedure".

.3	Measure overall A-weighted Sound Pressure Level

.4	Take minimum of one reading per 30 m2 of floor area, but no less than one reading in any one enclosed room or open area which will be occupied.

.5	Take measurements with system operating in its loudest normal condition which is typically the summer mode.

.6	Take measurements in rooms equipped with exhaust fans or unit heaters or cabinet heaters with fan “on” and fan “off” conditions.

.7	Measure sound pressure levels in rooms directly beneath roof top towers, condensers, furnaces, etc. with units running at maximum speed or capacity.

.8	Compare results with following maximum noise criteria:

.1	Conference Room, Observation/Therapy

Suite, First Aid Room, Classroom,

Lecture Halls, Executive Office:	[37] [  ] dB(A)

.2	Private Office, Library, Open Plan

Office, Gymnasium:	[42] [  ] dB(A)

.3	Cafeteria, Washrooms, Circulation/Waiting

Areas:	[47] [  ] dB(A)

.4	Computer Equipment Room, Kitchen,

Laboratory:	[52] [  ] dB(A)

.5	Light Maintenance Shops:	[57] [  ] dB(A)

.6	[                      ]:	[  ] dB(A)

3.9	BALANCING OF HYDRONIC SYSTEMS

.1	Fully open all valves, except the pressure bypass valve which must be closed, including balancing valves, isolation valves and control valves.

.2	Measure and record pump flows.

.3	Adjust flows through each boiler or chiller to ensure equal flow.

.4	Install pressure gauges across each coil or use balancing valve pressure tappings if provided. Read pressure drop through coil or balancing valve and set flow rate for full flow through coil. Set pressure drop across bypass valve at full flow to bypass to match coil full flow pressure drop.

.5	Distribute flow through radiation using circuit balancing valve pressure drop to apportion flow to each zone, and temperature drop to apportion flow through each run of radiation.

.6	Terminal reheat coils of constant or variable volume systems can not be hydronically balanced, by the method of air side temperature rise across the coil, until after air balance has been completed.

.7	Position and lock all balancing valves and mark all hand valves for design flow through all coils, coil by-passes, branch circuits, heat exchangers, chiller evaporators, etc. Record flow measurement data for all major circuits and each terminal device.

.8	After making all coil and terminal unit adjustments remeasure flow and head for each pump, for both single and parallel operation. Check flows through boilers, chillers, heat exchangers, etc. under following situations:

.1	With two pumps operating.

.1	Controls demanding maximum heating or cooling.

.2	Controls demanding no heating or cooling.

.2	With one pump operating - repeat for each pump:

.1	Controls demanding maximum heating or cooling.

.2	Controls demanding no heating or cooling.

.9	For each pump, plot maximum and minimum flows on curve for both single and parallel operation.

.10	Verify pressure drops and flows through pressure control by-pass valves over full operating range.

.11	Calibrate all pressure and temperature gauges.

3.10	BALANCING AND ADJUSTING OF [FIRE PUMP] [PRESSURE BOOSTER PUMPS]

.1	Record city water inlet pressure to pumps at two hour intervals for 48 hours in winter time. Repeat in summer period.

.2	Confirm in writing with utility company maximum and minimum anticipated pressure.

.3	Measure and record pressure at top of building.

.4	Adjust pressure in diaphragm type cushion tanks.

.5	Adjust bypass valve and pressure relief valve to accommodate installation and prevent pump overload on pressure.

.6	Run pumps for minimum of four hours and re-check pressure at top of building.

.7	Simulate and check following alarm conditions:

.1	Low utility company inlet pressure.

.2	High pressure.

.3	Pump overload.

3.11	BALANCING AND ADJUSTING OF DOMESTIC WATER SYSTEMS

.1	Adjust PRV on main line to 570 kPa maximum.

.2	Balance domestic hot water circulating system piping to ensure flow from all points in system. Ensure all hot and cold supply shut off valves are fully open.

3.12	BALANCING AND ADJUSTING OF EMERGENCY

GENERATOR SYSTEMS - AIR SIDE

.1	Adjust air flows to design.

.2	Measure air flows, static pressure drops.

.3	Measure discharge air temperature.

3.13	BALANCING REPORT

.1	Submit draft copies of final reports prior to Interim Acceptance of the Work. Provide four copies of final report for inclusion in Operation and Maintenance Manual.

.2	Include types, serial number and dates of calibration of instruments.

.3	Submit with report, fan and pump curves with operating conditions plotted. Submit grille and diffuser shop drawings and manufacturer's flow factors.

.4	Organize report as follows:

Air Systems

.1	Summary

.2	Procedure

.3	Instrumentation

.4	Drawings

.5	Equipment Summary

.6	Fan Data Sheets

.7	Fan Curves

.8	Air Handling Unit Profile Data

.9	Air Flow Measuring Station Data

.10 	Traverse Data and Schedule

.11 	Terminal Unit Summary

.12 	Outlet Data Summary and Schematic, per system

.13 	Building Pressurization Data

.14	Fire/smoke dampers verification

.15	[Smoke Control Systems]

.16 	Diagnostic

Hydronic Systems

.1	Summary

.2	Procedure

.3	Instrumentation

.4	Drawings

.5	Equipment Summary

.6	Pump Data Sheets

.7	Pump Curves

.8	Pump Profile Data

.9	Terminal Unit Summary

.10	Diagnostic

Acoustics

.1	Summary

.2	Procedure

.3	Instrumentation

.4	Drawings

.5	Sound Pressure Level Data

END OF SECTION