Section Cover Page

Section 23 31 13 2021-03-31 Ductwork

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Reference Documents

1.2	Alternatives

1.3	Definitions

1.4	Submittals

1.5	Quality Assurance

1.6	Delivery, Storage, and Handling

1.7	LEED Requirements

2.	Products

2.1	Materials

2.2	Fabrication

3.	Execution

3.1	Installation

3.2	Low Pressure Duct Thickness (Minimum)

3.3	Medium Pressure Duct Thickness

3.4	High Pressure Duct Thickness

3.5	Medium & High Pressure Duct Thicknesses

3.6	Oval Ductwork (Factory Made with Spiral Lock Seams)

3.7	Plenum Gauges

3.8	Fibrous Glass Ducts

3.9	Kitchen Exhaust Ducts

1.	General

1.1	REFERENCE DOCUMENTS

.1	American Society for Testing and Materials (ASTM):

| .1 | ASTM A653/A653M-09 | Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot Dip Process |
| --- | --- | --- |

.2	Canada Green Building Council (CaGBC):

| .1 | LEED v4 Rating System | Leadership in Energy and Environmental Design Website: www.cagbc.org |
| --- | --- | --- |

SPEC NOTE: Specify the above only if this is a LEED project

.3	National Fire Protection Association (NFPA):

| .1 | NFPA 90A-2009 | Standard for the Installation of Air Conditioning and Ventilation Systems |
| --- | --- | --- |
| .2 | NFPA 90B-2009 | Standard for the Installation of Warm Air Heating and Air Conditioning Systems |
| .3 | NFPA 96-2008 | Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations |

.4	Model National Energy Building Code of Canada for Buildings, 1997

SPEC NOTE: Specify the following IAQ requirements for LEED projects

.5	Sheet Metal and Air Conditioning National Contractors Association (SMACNA):

| .1 | SMACNA IAQ Guideline for Occupied Building Under Construction |
| --- | --- |

.6	South Coast Air Quality Management District, California State (SCAQMD):

| .1 | SCAQMD Rule 1168, Adhesive and Sealant Applications |
| --- | --- |

1.2	ALTERNATIVES

.1	Size round ducts installed in place of rectangular ducts indicated from ASHRAE table of equivalent rectangular and round ducts.  No variation of duct configuration of sizes permitted except by written permission.

1.3	DEFINITIONS

.1	Low Pressure:  Static pressure in duct less than 0.5 kPa and velocities less than 10 m/s.

.2	Medium Pressure:  Static pressure in duct less than 1.5 kPa and velocities greater than 10 m/s.

.3	High Pressure:  Static pressure over 1.5 kPa and less than 2.5 kPa and velocities greater than 10 m/s.

.4	Duct Sizes:  Inside clear dimensions.  For acoustically lined or internally insulated ducts, maintain sizes inside ducts.

1.4	SUBMITTALS

.1	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	Submit shop drawings and samples of duct fittings for approval, including particulars such as thicknesses, welds and configurations prior to start of work.

.2	Submit shop drawings for fibrous glass ducts including manufacturers fabrication and installation manual.

.2	Submit written inspection report of manufacturers acceptance of fabrication and installation of fibrous glass ductwork.  Confirm ductwork has been fabricated and installed in accordance with recommendations and SMACNA standards.  Inspection shall occur at beginning of installation.

1.5	QUALITY ASSURANCE

.1	Ductwork shall meet the requirements of NFPA 90A, Air Conditioning and Ventilating Systems [,  NFPA No. 90B, Standard for the Installation of Warm Air Heating and Air Conditioning Systems] [and NFPA No. 96, Standard for the Installation of Equipment for the Removal of Smoke and Grease-Laden Vapours from Commercial Cooking Equipment].

.2	Fabricate in accordance with SMACNA duct manuals and ASHRAE handbooks.

1.6	Delivery, storage, and handling

.1	Separate waste materials for [reuse] [and] [recycling] in accordance with Section 01 74 19 – Waste Management and Disposal.

SPEC NOTE: Delete the following if LEED certification is not being pursued or if the individual credits are not being pursued.

1.7	leed requirements

.1	EQ Credit 3.1 – Construction IAQ Management Plan: During Construction

.1	Objective: Prevent indoor air quality problems resulting from the [construction] [renovation] process in order to help sustain the comfort and well-being of construction workers and building occupants.

.2	Requirements: Meet or exceed the recommended Design Approaches of SMACNA IAQ Guidelines for Occupied Buildings Under Construction, Chapter

.1	During construction use filtration media with a Minimum Efficiency Reporting Value (MERV) of 8 at each return air grill.  Replace filtration media prior to occupancy.

.2	Protect stored on-site and installed absorptive materials from moisture damage.

.2	EQ Credit 4.1 – Low-Emitting Materials: Adhesives & Sealants

.1	Duct sealants and adhesives must be less than the VOC content limits as indicated in the State of California’s South Coast Air Quality Management District (SCAQMD) Rule 1168.

2.	Products

2.1	MATERIALS

.1	Ducts:  Galvanized steel lock forming quality, having galvanized coating to ASTM A653M, G90 designation for both sides.

.2	Fasteners:  Use rivets and bolts throughout; sheet metal screws accepted on low pressure ducts.

.3	Sealant:  Water resistant, fire resistive, compatible with mating materials.

.4	Flexible Ducts:  Corrugated aluminum or fabric supported by helically wound steel wire or flat steel strips.

.5	Flexible Fibrous Glass Ducts:  Flexible duct wrapped with flexible fibrous glass insulation, enclosed by seamless aluminum pigmented plastic vapour barrier jacket, "K" value at 24°C maximum 0.033 W/m.°C

.6	Fibrous Glass Duct:  25 mm thick rigid fibrous glass with aluminum foil, glass scrim and kraft or plastic jacket vapour barrier, "K" value at 24°C maximum 0.033 W/m.°C

.7	Kitchen Exhaust Ducts:  Minimum 1.6 mm galvanized steel or 1.2 mm stainless steel with welded joints.

2.2	FABRICATION

.1	Complete metal ducts with themselves with no single partition between ducts.  Where width of duct exceeds 450 mm cross break for rigidity.  Open corners are not acceptable.

.2	Lap metal ducts in direction of air flow.  Hammer down edges and slips to leave smooth duct interior.

.3	Construct tees, bends, and elbows with radius of not less than 1 1/2 times width of duct on centre line.  Where not possible and where rectangular elbows used, provide approved type air foil turning vanes.  Where acoustical lining is provided, provide turning vanes of perforated metal type with fibreglass inside.

.4	Increase duct sizes gradually, not exceeding 15 degree divergence wherever possible.  Maximum divergence upstream of equipment to be 30 degree and 45 degree convergence downstream.

.5	Rigidly construct metal ducts with joints mechanically tight, substantially airtight, braced and stiffened so as not to breathe, rattle, vibrate or sag.  Caulk duct joints and connections with sealant as ducts are being assembled.

.6	Provide easements where low pressure ductwork conflicts with piping and structure where easements exceed 10% duct area, split into two ducts maintaining original duct area.

.7	Provide necessary baffling in mixed air plenums to ensure good mixed air temperature with variations of not more than ± 15°C under all operating conditions.

.8	Fabricate continuously welded medium and high pressure round and oval duct fittings of one gauge heavier than gauges indicated for duct size.  Joints shall be 100 mm cemented slip joint, brazed or electric welded.  Prime coat welded joints.  Fabricate elbows of five piece construction.  Provide standard 45° take-offs unless otherwise indicated where conical 90° tee take-off connections may be used.  Adequately brace with truss couplings or comparison angle flanges with asbestos free gaskets bolted at 150 mm centers.

.9	Fabricate plenums and casings to configurations shown on drawings.  Construct plenums of galvanized panels joined standing seams on outside of casing riveted or bolted on approximately 300 mm centers.  Reinforce with suitable angles and provide diagonal bracing as required.  Tightly fit at apparatus and caulk with sealant.

.10	Provide 75 mm reinforced concrete curb for plenum walls and floor mounted casings.  At floor, rivet panels on 200 mm centers to angles.  Where floors are acoustically insulated, provide liner at 1.2 mm galvanized expanded metal mesh, turned up 300 mm at sides with sheet metal shields.

.11	Reinforce door frames with angle iron tied to horizontal and vertical plenum supporting angles.  Install hinged access doors where shown, specified or where required for access to equipment for cleaning and inspection.

.12	Fabricate acoustic plenums of galvanized steel.  Provide 1.6 mm back facing and 0.8 mm perforated front facing with 3 mm diameter holes on 4 mm centers.  Construct panels 75 mm thick packed with 72 kg/m3 minimum fibrous glass media, on inverted channels of 1.6 mm [on 75 mm reinforced concrete curb].

.13	Fabricate fibrous glass ducts and fittings by fabrication machine.  Make only minor on site manual adjustments.  Wipe clean surfaces being joined.  Join with heat activated chemical bonding closure strip [equal to Johns-Manville ThermLock closure system.  Provide at duct support locations, an extra wrapping of closure strip].

.14	Fabricate seams and joints in kitchen exhaust ducts liquid tight with continuous external welds.

3.	Execution

3.1	INSTALLATION

.1	Provide openings in ductwork where required to accommodate thermometers and controllers.  Provide pivot tube openings where required for testing of systems, complete with metal can with spring device or screw to ensure against air leakage.  Where openings are provided in insulated ductwork, install insulation material inside a metal ring.

.2	Clean duct systems and force air at high velocity through duct to remove accumulated dust.  To obtain sufficient air, clean half the system at a time.  Protect equipment which may be harmed by excessive dirt with filters, or bypass during cleaning.

.3	Clean duct systems with high power vacuum machines.  Protect equipment which may be harmed by excessive dirt with filters, or bypass during cleaning.  Provide adequate access into ductwork for cleaning purposes.

SPEC NOTE:  Specify 3.1.2 or 3.1.3, not both.

.4	Locate ducts with sufficient space around equipment to allow normal operating and maintenance activities.

.5	Slope underground ducts to plenums or low pumpout points at 2 mm per metre.  Provide access doors for inspection.  Encase ducts in 80 mm minimum of concrete.  Provide adequate tie-down points to prevent ducts from floating during concrete pour.  Introduce no heat into ducts until 20 days after pouring of concrete.

.6	Coat underground ducts with one coat [and seams and joints with additional coat] of asphalt solvent base protective coating [,  Flinkote PC-19].  [Insulate supply duct runs over 21 m long with 25 mm thick insulation covered with plastic vapour barrier].

.7	Provide floor drains in fresh air and humidifier sections with deep seal traps.

.8	Set plenum doors 150 mm to 300 mm above floor.  Arrange door swings so that fan static holds door in closed position.

.9	Connect terminal units to medium or high pressure ducts with 300 mm maximum length of flexible duct.  Do not use flexible duct to change direction.

.10	Connect diffusers or troffer boots to low pressure ducts with 1.5 m maximum length of flexible duct.  Hold in place with caulking compound and strap or clamp.

3.2	LOW PRESSURE DUCT THICKNESSES (MINIMUM)

.1	Rectangular Ducts

| Maximum Width | mm |
| --- | --- |
| Up to 300 mm | 0.6 |
| 330 mm to 760 mm | 0.8 |
| 790 mm to 1370 mm | 0.8 |
| 1400 mm to 2130 mm | 1.0 |
| 2160 mm and Over | 1.2 |

.2	Round Ducts

| Duct Diameter | mm |
| --- | --- |
| Up to 330 mm | 0.6 |
| 350 mm to 550 mm | 0.8 |
| 580 mm to 1270 mm | 0.8 |
| 890 mm to 910 mm | 1.0 |
| 1300 mm to 1520 mm | 1.2 |
| 1550 mm to 2130 mm | 1.6 |

.3	Underground Ducts

| Duct Diameter | Spiral Lock Seam mm | Longitudinal Seam mm |
| --- | --- | --- |
| Up to 380 mm | 0.8 | 0.8 |
| 400 to 510 mm | 0.8 | 1.0 |
| 530 to 890 mm | 1.0 | 1.2 |
| Over 910 mm | 1.2 | 1.6 |

3.3	MEDIUM PRESSURE DUCT THICKNESS

.1	Rectangular Ductwork

| Maximum | mm |
| --- | --- |
| Up to 460 mm | 0.8 |
| 480 mm to 1220 mm | 0.8 |
| 1250 mm to 1830 mm | 1.0 |
| 1850 mm to 2440 mm | 1.2 |
| 2460 mm and Over | 1.6 |

3.4	HIGH PRESSURE DUCT THICKNESSES

.1	Rectangular Ductwork

| Maximum Width | mm |
| --- | --- |
| Up to 460 mm | 0.8 |
| 480 mm to 1220 mm | 1.0 |
| 1250 mm to 1830 mm | 1.2 |
| 1850 mm to 2440 mm | 1.6 |
| 2460 mm to 3660 mm | 2.0 |

3.5	MEDIUM & HIGH PRESSURE DUCT THICKNESSES

| .1 | Round Ducts | Spiral Lock Seam mm | Longitudinal Seam mm |
| --- | --- | --- | --- |
|  | Up to 200 mm | 0.6 | 0.8 |
|  | 230 to 560 mm | 0.8 | 0.8 |
|  | 580 to 910 mm | 0.8 | 1.0 |
|  | 940 to 1270 mm | 1.0 | 1.0 |
|  | 1300 to 1520 mm | 1.2 | 1.2 |
|  | 1550 mm and Over | 1.6 | 0.6 |

3.6	OVAL DUCTWORK (FACTORY MADE WITH SPIRAL LOCK SEAMS)

| .1 | Maximum Width | mm | Centers | Reinforcement |
| --- | --- | --- | --- | --- |
|  | Up to 500 mm | 0.8 |  | none |
|  | 280 to 500 mm | 0.8 | 1220 mm | L50 x 50 x 3 mm |
|  | 530 to 1020 mm | 1.2 | 760 mm | L50 x 50 x 5 mm |
|  | 1040 to 1830 mm | 1.6 | 600 mm | L75 x 75 x 5 mm |

3.7	PLENUM GAUGES

.1	Fabricate fan plenums and plenums downstream of fan in accordance with duct gauges.

.2	Fabricate plenums upstream of fan between apparatus of 1.6 mm.

.3	Fabricate plenums upstream of filters of 1.2 mm

3.8	FIBROUS GLASS DUCTS

.1	Fibrous glass ductwork may be substituted for internally or externally insulated or uninsulated low pressure sheet metal ductwork.

3.9	KITCHEN EXHAUST DUCTS

.1	Protect galvanized ductwork exposed to outside elements by painting or coating with suitable weather resistant material.

.2	Provide residue traps at base of vertical risers with provisions for cleanout.

END OF SECTION