Section Cover Page

Section 23 51 00 2010-12-31 Breeching and Chimneys

Use this Section to specify breeching and chimneys.  This section is limited to venting systems constructed of factory-built chimney components.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet - Reference Standards

.3	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Reference Documents

1.3	Product Options and Substitutions

1.4	Definitions

1.5	Quality Assurance

1.6	Submittals

1.7	Coordination

1.8	Delivery, Storage, and Handling

2.	Products

2.1	Vents

2.2	Breeching

2.3	Refractory Lining

2.4	Accessories

3.	Execution

3.1	Vent Installation

3.2	Vent Schedule

1.	General

1.1	RELATED REQUIREMENTS

.1	Membrane roofing penetrations:	Division 07.

.2	Mechanical General Requirements:	Section 23 00 13.

.3	Ductwork and Breeching Insulation:	Section 23 07 00.

1.2	REFERENCE DOCUMENTS

.1	American Society for Testing and Materials (ASTM):

| .1 | ASTM C401-91 (2005) | Standard Classification of Alumina and Alumina-Silicate Castable Refractories |
| --- | --- | --- |

.2	Canadian Standards Association (CSA):

| .1 | CAN/CSA B149.1-05 | Natural Gas and Propane Installation Code |
| --- | --- | --- |
| .2 | CAN/CSA B149.2-05 | Propane Storage and Handling Code |

.3	Underwriters Laboratories of Canada (ULC):

| .1 | CAN/ULC-S604-M91 | Standard for Factory Built, Type A Chimneys |
| --- | --- | --- |
| .2 | CAN/ULC-S605-M91 | Standard for Gas Vents |
| .3 | CAN/ULC-S609-M89 | Standard for Low Temperature Vents, Type L |
| .4 | CAN/ULC-S629-M87 | Standard for 650°C Factory Built Chimneys |

1.3	PRODUCT OPTIONS AND SUBSTITUTIONS

.1	Refer to Division 01 for requirements pertaining to product options and substitutions.

1.4	DEFINITIONS

.1	Vent:  an enclosed passageway for conveying flue gases from the appliances to outdoors.

.2	Breeching:  the portion of vent from the appliance to the chimney.

.3	Chimney:  a primarily vertical portion of vent.

.4	Draft:  the flow of air or combustion products or both, through an appliance and its venting system.

.5	Mechanical Draft:  a draft produced by a mechanical device such as a fan, blower, or aspirator which may supplement natural draft.

.6	Forced Draft:  a mechanical draft produced by a device upstream of the combustion zone of an appliance.

.7	Induced Draft:  a mechanical draft produced by a device downstream from the combustion zone of an appliance.

.8	Natural Draft:  a draft other than mechanical draft.

1.5	QUALITY ASSURANCE

.1	Vents and accessories forming part of the venting system shall be ULC labelled.

1.6	submittals

.1	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	Indicate the following information:

.1	Methods of sealing sections.

.2	Methods of expansion.

.3	Details of thimbles.

.4	Bases/Foundations.

.5	Supports.

.6	Guy details.

.7	Rain caps.

.2	Closeout Submittals:

.1	Submit operations and maintenance data for incorporation into manuals specified in Section 20 01 06 – Mechanical Operation and Maintenance Manual.

1.7	COORDINATION

.1	Coordinate counterflashing work with flashing work detailed on membrane roofing detail drawings.

1.8	Delivery, Storage, and Handling

.1	Separate waste materials for [reuse] [and] [recycling] in accordance with Section 01 74 19 – Waste Management and Disposal.

2.	Products

2.1	VENTS

.1	Type A:  to CAN/ULC-S604.

.1	Application:  gas and liquid fuel fired appliances.

.2	Service Temperature:  maximum flue gas temperature of 540°C.

.2	Type A-2 Vent:  to CAN/ULC-S629.

.1	Application:  gas, liquid and solid fuel fired appliances.

.2	Service Temperature:  maximum flue gas temperature of 650°C.

.3	Type B Vent:  to CAN/ULC-S605.

.1	Application:  gas fired appliances certified with draft hoods or divertors.

.2	Service Temperature:  maximum flue gas temperature of 243°C.

.4	Type BW Vent:  to CAN/ULC-S605.

.1	Application:  gas fired recessed heaters.

.2	Service Temperature:  maximum flue gas temperature of 243°C.

.5	Type L Vent:  to CAN/ULC-S609.

.1	Application:  fuel burning appliances certified for use with Type L vents.

.2	Service Temperature:  maximum flue gas temperature of 298°C.

2.2	BREECHING

.1	Breeching Type 1:  for natural draft, gas burning appliances with draft hoods, use one of the following:

.1	Galvanized steel with thicknesses as follows:

| Vent Diameter | Min. Thickness |
| --- | --- |
| Smaller than 125 mm | 0.4 mm |
| 125 mm to 200 mm | 0.5 mm |
| Larger than 200 mm | 0.6 mm |

.2	Breeching constructed of same vent components as chimney.

.2	Breeching Type 2:  for forced, induced, or natural draft with dilution, gas or liquid fuel fired appliances, use one of the following:

.1	Mild steel, all welded construction with thicknesses as follows:

| Vent Diameter | Min. Thickness |
| --- | --- |
| 300 mm and smaller | 1.2 mm |
| 325 mm to 600 mm | 1.6 mm |
| 625 mm to 900 mm | 2.0 mm |
| 925 mm and larger | 3.0 mm |

.2	Breeching constructed of same vent components as chimney.

.3	Breeching Type 3:  for solid fuel fired appliances, use one of the following:

.1	Mild steel, minimum thickness of 3 mm, all welded constructed, lined with 50 mm thick castable refractory.

.2	Breeching constructed of same vent components as chimney.

2.3	REFRACTORY LINING

.1	High temperature castable lining:  to ASTM C401, Class C, High Strength and as follows:

.1	Service Temperature:  1350°C.

.2	Thermal Conductivity ("k"):  0.85 W/m°C at 1100°C.

.3	Density:  1874 kg/m3.

.4	Composition:

.1	Al2O3:  47%

.2	SiO2:   37%

2.4	ACCESSORIES

.1	Cleanouts:  bolted, gasketted type, full size of breeching area.

.2	Barometric Damper:  [single acting] [double acting] sized to 70% of full size of breeching area.

SPEC NOTE:  Use single acting barometric dampers only on incinerators.

.3	Breeching Damper:  motor operated damper 3.5 mm thick steel, ball bearings on full length shaft, 80% maximum closure.

.4	Appurtenances:  raincap, thimbles, support brackets and guys, flashing and counter flashings, fly ash screen, and other materials required to complete the assembly.

3.	Execution

3.1	VENT INSTALLATION

.1	Install vents, complete with accessories and appurtances, in accordance with [CAN/CGA B149.1 and Alberta amendments], [CAN/CGA B149.2 and Alberta amendments] [          ] Alberta Building Code, manufacturer's instructions and as follows:

SPEC NOTE:  Specify CAN/CGA B149.1 were natural gas fired appliances are used and CAN/CGA B149.2-M95 were propane fired appliances are used.

.1	Type A:  to CAN/ULC-S604.

.2	Type A-2:  to CAN/ULC-S629.

.3	Type B:  to CAN/ULC-S605.

.4	Type BW:  to CAN/ULC-S605.

.5	Type L:  to CAN/ULC S609.

.2	Do not penetrate flue gas chamber of vent with screws or mechanical fasteners.

.3	Install breeching with positive slope upward from appliance.

.4	Suspend breeching using trapeze hangers at 1500 mm centers.

.5	Install cleanout at base of chimney.

SPEC NOTE:  Include following only when required by system design.

.6	[Provide barometric damper as indicated on drawings.]

.7	[Provide breeching damper as indicated on drawings.]

.8	Support chimney at bottom, roof and intermediate levels.

.9	Install thimbles where penetrating roof, floor, ceiling and where breeching enters masonry chimney.

.10	Install fly ash screen on all chimneys serving solid fuel fired appliances.

.11	Install raincap on chimney outlet.

.12	Install counterflashing where chimneys pass through roof.

.13	Provide for expansion and contraction of chimney and breeching.

3.2	VENT SCHEDULE

| Tag No. Appliance | Appliance Input Rating (kW) | Flue Temp (°C) | Draft Type | Fuel Type | Vent Type | Breeching Type |
| --- | --- | --- | --- | --- | --- | --- |

SPEC NOTE:  List all types of fuel fired equipment on the schedule.

# END OF SECTION