Section Cover Page

Section 23 51 00 2008-05-01 Breeching and Chimneys

Use this Section to specify breeching and chimneys.  This section is limited to venting systems constructed of factory-built chimney components.

This Master Specification Section contains:

.1	This Cover Page

.2	Data Sheet - Reference Documents

.3	Specification Section Text:

1.	General

1.1	Related Work Specified in Other Sections

1.2	Product Options and Substitutions

1.3	Definitions

1.4	Quality Assurance

1.5	Shop Drawings

1.6	Coordination

2.	Products

2.1	Vents

2.2	Breeching

2.3	Accessories

3.	Execution

3.1	Vent Installation

3.2	Vent Schedule

Applicable Standards:

.1	CAN/CGA-B149.1-M91	Natural Gas Installation Code

.2	CAN/CGA-B149.2-M91	Propane Installation Code

.3	CAN/ULC-S604-1991	Factory Built, Type A Chimneys

.4	CAN/ULC-S605-1991	Gas Vents

.5	CAN/ULC-S609-1989	Low Temperature Vents, Type L

.6	CAN/ULC-S629-1987	650oC Factory Built Chimneys

END OF DATA SHEETS

1.	General

1.1	RELATED WORK SPECIFIED IN OTHER SECTIONS

.1	Membrane roofing penetrations:	Division 07.

.2	Ductwork and Breeching Insulation:	Section 23 07 00.

1.2	PRODUCT OPTIONS AND SUBSTITUTIONS

.1	Refer to Division 01 for requirements pertaining to product options and substitutions.

1.3	DEFINITIONS

.1	Vent:  an enclosed passageway for conveying flue gases from the appliances to outdoors.

.2	Breeching:  the portion of vent from the appliance to the chimney.

.3	Chimney:  a primarily vertical portion of vent.

.4	Draft:  the flow of air or combustion products or both, through an appliance and its venting system.

.5	Mechanical Draft:  a draft produced by a mechanical device such as a fan, blower, or aspirator which may supplement natural draft.

.6	Forced Draft:  a mechanical draft produced by a device upstream of the combustion zone of an appliance.

.7	Induced Draft:  a mechanical draft produced by a device downstream from the combustion zone of an appliance.

.8	Natural Draft:  a draft other than mechanical draft.

1.4	QUALITY ASSURANCE

.1	Vents and accessories forming part of the venting system shall be ULC labelled.

1.5	SHOP DRAWINGS

.1	Comply with requirements of Section 20 00 13.

1.6	COORDINATION

.1	Coordinate counterflashing work with flashing work detailed on membrane roofing detail drawings.

2.	Products

2.1	VENTS

.1	Type A:  to CAN/ULC-S604-1994, Factory Built, Type A Chimneys.

.1	Application:  gas and liquid fuel fired appliances.

.2	Service Temperature:  maximum flue gas temperature of 540oC.

.2	Type B Vent:  to CAN/ULC-S605-1991, Gas Vents.

.1	Application:  gas fired appliances certified with draft hoods or divertors.

.2	Service Temperature:  maximum flue gas temperature of 243oC.

SPEC NOTE:  Include the items .3 and .4 only when type BW and type L vents are required.

.3	Type BW Vent:  to CAN/ULC-S605-1991, Gas Vents.

.1	Application:  gas fired recessed heaters.

.2	Service Temperature:  maximum flue gas temperature of 243oC.

.4	Type L Vent:  to CAN/ULC-S609-1989, Low Temperature Vents.

.1	Application:  fuel burning appliances certified for use with Type L vents.

.2	Service Temperature:  maximum flue gas temperature of 298oC.

2.2	BREECHING

.1	Breeching Type 1:  for natural draft, gas burning appliances with draft hoods, use one of the following:

.1	Galvanized steel with thicknesses as follows:

| Vent Diameter | Min. Thickness |
| --- | --- |
| Smaller than 125 mm | 0.4 mm |
| 125 mm to 200 mm | 0.5 mm |
| Larger than 200 mm | 0.6 mm |

.2	Breeching constructed of same vent components as chimney.

SPEC NOTE:  Include the following items .2 and .3 only when breeching type 2 and type 3 are required.

.2	Breeching Type 2:  for forced, induced, or natural draft with dilution, gas or liquid fuel fired appliances, use one of the following:

.1	Mild steel, all welded construction with thicknesses as follows:

| Vent Diameter | Min. Thickness |
| --- | --- |
| 300 mm and smaller | 1.2 mm |
| 325 mm to 600 mm | 1.6 mm |
| 625 mm to 900 mm | 2.0 mm |
| 925 mm and larger | 3.0 mm |

.2	Breeching constructed of same vent components as chimney.

.3	Breeching Type 3:  for solid fuel fired appliances, use one of the following:

.1	Mild steel, minimum thickness of 3 mm, all welded constructed, lined with 50 mm thick castable refractory.

.2	Breeching constructed of same vent components as chimney.

2.3	ACCESSORIES

.1	Cleanouts:  bolted, gasketted type, full size of breeching area.

.2	Barometric Damper:  double acting sized to 70% of full size of breeching area.

.3	Breeching Damper:  motor operated damper 3.5 mm thick steel, ball bearings on full length shaft, 80% maximum closure.

.4	Appurtenances:  raincap, thimbles, support brackets and guys, flashing and counter flashings, fly ash screen, and other materials required to complete the assembly.

3.	Execution

3.1	VENT INSTALLATION

.1	Install vents, complete with accessories and appurtenances, in accordance with [CAN/CGA-B149.1-M91, Natural Gas Installation Code] [CAN/CGA-B149.2-M91, Propane Installation Code,] Alberta Building Code, manufacturer's instructions and as follows:

SPEC NOTE:  Specify CAN/CGA-B149.1-M91 where natural gas fired appliances are used and CAN/CGA-B149.2-M91 where propane fired appliances are used.

.1	Type A:  to CAN/ULC-S604-1991, Factory Built, Type A Chimneys.

.2	Type A-2:  to CAN/ULC-S629-1987, 650oC Factory Built Chimneys.

.3	Type B:  to CAN/ULC-S605-1991, Gas Vents.

.4	Type BW:  to CAN/ULC-S605-1991, Gas Vents.

.5	Type L:  to CAN/ULC S609-1989, Low Temperature Vents, Type L.

.2	Do not penetrate flue gas chamber of vent with screws or mechanical fasteners.

.3	Install breeching with positive slope upward from appliance.

.4	Suspend breeching using trapeze hangers at 1500 mm centers.

.5	Install cleanout at base of chimney.

.6	Support chimney at bottom, roof and intermediate levels.

.7	Install thimbles where penetrating roof, floor, ceiling and where breeching enters masonry chimney.

.8	Install fly ash screen on all chimneys serving solid fuel fired appliances.

.9	Install raincap on chimney outlet.

.10	Install counterflashing where chimneys pass through roof.

.11	Provide for expansion and contraction of chimney and breeching.

SPEC NOTE:  Include barometric or breeching dampers when required by system design, and indicated on drawings.

.12	Provide barometric damper as indicated on drawings.

.13	Provide breeching damper as indicated on drawings.

3.2	VENT SCHEDULE

| Tag No. Appliance | Appliance Input Rating (kW) | Flue Temp (oC) | Draft Type | Fuel Type | Vent Type | Breeching Type |
| --- | --- | --- | --- | --- | --- | --- |

SPEC NOTE:  List all types of fuel fired equipment on the schedule.

END OF SECTION