Section Cover Page

Section 23 81 19 Packaged Roof Top 2008-05-01 Heating/Cooling Units

Use this section to specify Packaged Roof Top Heating and Cooling Units, or units with cooling only.  Delete the word "Heating" from the header and delete all reference to heating in the specification, when the roof equipment is cooling only.

This Master Specification Section contains:

.1	This Cover Page

.2	Specification Section Text:

1.	General

1.1	Quality Assurance

2.	Products

2.1	Type

2.2	Construction

2.3	Burner

2.4	Evaporator Coil

2.5	Compressor

2.6	Condenser

2.7	Supply/Return Casing

2.8	Operating Controls

2.9	Remote Panel

3.	Execution

3.1	Installation

3.2	Packaged Roof Top Heating Cooling Units Schedule

1.	General

1.1	QUALITY ASSURANCE

.1	Meet the requirements of CSA, Provincial and Municipal Codes and be CSA listed.

.2	Units shall be products of manufacturers who provide local service personnel from factory representative, franchised dealer or certified maintenance service shop.

2.	Products

2.1	TYPE

.1	Provide roof mounted type units with [gas burner] [and refrigeration].

.2	Units shall be self-contained, packaged, factory assembled and prewired consisting of a cabinet and frame, supply fan, controls, air filer, economizer section, [return fan,] [heat exchanger and burner,] [compressor, condenser and cooling  coil].

2.2	CONSTRUCTION

.1	Cabinet:  Baked enamel finish, easily removed access doors or panels with quick fasteners, [locking door handle type,] [screwdriver operated flush cam type].

.2	Insulation:  Neoprene coated glass fiber on surfaces where conditioned air is handled. Protect edges from erosion.

.3	Supply [and Return] Fan:  Rubber isolated hinge mounted motor. Complete fan assembly shall be isolated.

.4	Air Filters:  25 mm thick glass fiber disposable media in metal frames arranged for easy replacement.

SPEC NOTE:  Include this item when a heat exchanger is required.

[.5	Heat Exchangers:  [Aluminized] [Stainless] steel of welded construction.]

SPEC NOTE:  Include item 2.3 when heating is required.

2.3	BURNER

.1	Gas Burner:  Forced or induced draft type with adjustable combustion air supply, pressure regulator, gas valves, manual shut-off, intermittent spark or glow coil ignition, flame sensing device and automatic 100% shut-off and gas burner safety controls.

.2	High Limit Control:  With fixed stop at maximum permissible setting.

.3	Control Supply Fan:  Include switch for continuous fan operation.

SPEC NOTE:  Include item 2.4 and 2.5 when cooling is required.

2.4	EVAPORATOR COIL

.1	Provide copper tube aluminum fin coil assembly with galvanized drain pan and connection, capillary tubes and expansion valve.

2.5	COMPRESSOR

.1	Provide hermetic or semi-hermetic compressor, 3600 r/min maximum, resiliently mounted with positive lubrication, crankcase heater, high and low pressure safety controls, motor overload protection, service valves and filter drier.

.2	Timed off-circuit shall provide a minimum of 5 minutes between starts.

.3	Outdoor thermostat shall energize compressor above 14°C ambient.

.4	Provide step capacity control by [cycling the compressors] [cylinder unloading]. Do not use hot gas bypass.

2.6	CONDENSER

.1	Provide copper tube aluminum fin coil assembly with sub-cooling rows.

.2	Provide direct drive axial fans, resiliently mounted with fan guard, motor overload protection, wired to operate with compressor.

2.7	SUPPLY/RETURN CASING

.1	Provide economize section.

.2	Provide outside, return and relief dampers with damper operator and control package to automatically vary outside air quantity.

.3	Provide tight fitting dampers with neoprene or suitable edge gaskets.

.4	Damper Operator:  spring return with motor and gear train sealed in oil.

.5	Mixed Air Controls:  Maintain selected mixed air temperature, lock out compressor below approximately 14oC ambient.

2.8	OPERATING CONTROLS

.1	Adjustable thermostat shall control [heating stages in sequence with delay between stages] [compressor and condenser fan] and supply fan to maintain temperature setting.

.2	Thermostat shall include system selector switch, heat-cool-off and fan control switch, on-auto.

.3	[Double] [Single] acting thermostat shall have minimum [[     ] stage heating and] [     ] stage cooling.

.4	Provide in supply air low limit thermostat to [close outside air damper and] stop supply fan.

.5	Locate thermostat in [room         ] [supply air return air].

.6	Provide programmable thermostat with 4 programs/day, 1 week cycle to provide program of temperature control settings.

2.9	REMOTE PANEL

.1	Provide remote readout panels containing:  signal lights indicating system status, [heating system failure,] [cooling system failure] and dirty filters; check switches  proving signal light operation; system on-off switch, [cooling system on-off switch].

.2	Provide gauges in remote panel to indicate supply and mixed air temperature.

3.	Execution

3.1	INSTALLATION

.1	Mount units on curbs to provide watertight enclosure to protect ductwork and utility services.

3.2	PACKAGED ROOF TOP [HEATING] COOLING UNITS SCHEDULE

|  | RT-1 | RT-2 |
| --- | --- | --- |
| Location | [ ] | [ ] |
| Manufacturer | [ ] | [ ] |
| Model [ ] | [ ] | [ ] |
| Supply Air L/s | [ ] | [ ] |
| Supply external static pressure kPa | [ ] | [ ] |
| Supply Motor kW | [ ] | [ ] |
| [Return Air L/s] | [ ] | [ ] |
| [Return external static pressure kPa] | [ ] | [ ] |
| [Return Motor kW] | [ ] | [ ] |
| Sensible Cooling kW Total Cooling kW | [ ] [ ] | [ ] [ ] |
| Coil Entering oC DB/WB | [ ] | [ ] |
| Heating Input kW Heating Output kW | [ ] [ ] | [ ] [ ] |

END OF SECTION