Section Cover Page

Section 23 82 05 2008-05-01 Terminal Heat Transfer Units

This Master Specification Section contains:

.1	This Cover Page

.2	Specification Section Text:

1.	General

1.1	Quality Assurance

1.2	Submittals

1.3	Related Requirements

2.	Products

2.1	General

2.2	Baseboard Radiation

2.3	Wall Fin Radiation

2.4	Convectors

2.5	Unit Heaters

2.6	Fancoil Units

3.	Execution

3.1	Installation

3.2	Performance

3.3	Radiation and Convector Schedule

3.4	Cabinet and Unit Heater Schedule

1.	General

1.1	QUALITY ASSURANCE

.1	Terminal heat transfer units shall be product of manufacturer regularly engaged in production of such units.

1.2	SUBMITTALS

.1	Submit, in addition to shop drawings, schedules of radiation heating elements and enclosure indicating length and number of pieces of element and enclosure, corner pieces, end caps, cap strips, access doors, pilaster covers and a comparison of specified heat required to actual heat output provided.

1.3	RELATED REQUIREMENTS

.1	Painting of Mechanical and Electrical Work	Section 09 91 30

2.	Products

2.1	GENERAL

.1	For each convection type heating unit not thermostatically controlled, provide knob-operated internal damper at enclosure air outlet grille.  Group rooms in zones on one thermostat and provide dampers in each room.

.2	Factory apply baked prefinished on metal surfaces of enclosure or cabinet.

2.2	BASEBOARD RADIATION

.1	Heating Elements:  20 mm nominal copper tubing mechanically expanded into flanged collars of evenly spaced aluminum fins, one tube end belled.

.2	Enclosure:  Minimum 0.8 mm steel with back and top of one piece, front panel, end caps, corners and joiner pieces to snap together, front panel easily removable, full length damper. Provide wall to wall installation unless otherwise indicated on the drawings.

.3	Element Brackets:  1.2 mm galvanized steel.

2.3	WALL FIN RADIATION

.1	Heating Elements:  30 mm seamless copper tubing, 1 mm minimum wall thickness, mechanically expanded into evenly spaced aluminum fins, suitable for sweat fittings.

.2	Element Hangers:  Quiet operating, ball bearing cradle type.

.3	Enclosures:  1.2 mm steel up to 450 mm in height, 1.6 mm steel over 450 mm in height c/w easily jointed components for wall to wall installation. Support rigidly, top and bottom, on wall mounted brackets at 900 mm centres maximum.

2.4	CONVECTORS

.1	Heating Elements:  Seamless copper tubing mechanically expanded into evenly spaced aluminum fins.

.2	Cabinet:  1.6 mm steel front and top, 1.2 mm steel back and ends.

2.5	UNIT HEATERS

.1	Casing:  1.2 mm steel with threaded connections for hanger rods.

.2	Coils:  Seamless copper tubing, 0.6 mm minimum wall thickness, silver brazed to steel headers, and with evenly spaced aluminum fins mechanically bonded to tubing.

.3	Fan:  Direct drive propeller type, statically and dynamically balanced.

.4	Air Outlet:  Adjustable pattern diffuser on projection models and four-way louvers on horizontal throw models.

2.6	FANCOIL UNITS

.1	Cabinet:  1.6 mm steel with easily removed panels, glass fiber insulation, integral air outlet and inlet grilles.  Finish exposed surfaces in baked enamel of approved colour.

.2	Coils:  Evenly spaced aluminum fins mechanically bonded to copper tubes.

.3	Fans:  Centrifugal forward curved double width wheels, statically and dynamically balanced, direct driven, on sleeve bearings resiliently mounted.

.4	Filter:  Easily removed 25 mm thick glass fiber throw-away or permanent washable type filtering air before coil.

.5	Control:  4 position speed switch factory wired. 2 speed switch located in cabinet where accessible. Provide key operated wall mounted switch where inaccessible.

3.	Execution

3.1	INSTALLATION

.1	Provide each unit with shut-off valve on supply and lockshield balancing valve on return piping.

.2	Provide each unit at high points with easily accessible manual air vent. If not easily accessible, extend vent to exterior surface of cabinet for easy servicing. For fan coil units and unit heaters provide float operated automatic air vents with stop valve.

.3	For inaccessible valves, provide factory-made permanently hinged access doors, 150 x 180 mm minimum size, integral with cabinet.

3.2	PERFORMANCE

.1	Radiation and convector capacities are based on 18 degrees celsius entering air temperature, 82 degrees celsius average water temperature.

.2	Unit heater and fancoil capacities are based on 16 degrees celsius entering air temperature, 82 degrees celsius entering water temperature.

3.3	RADIATION AND CONVECTOR SCHEDULE

| Type |  |
| --- | --- |
| Manufacturer |  |
| Model |  |
| Enclosure |  |
| Rows |  |
| kW/m |  |
| Remarks |  |

3.4	CABINET AND UNIT HEATER SCHEDULE

| Unit No. |  |
| --- | --- |
| Location |  |
| Service |  |
| Manufacturer |  |
| Model |  |
| kW |  |
| L/s |  |
| Motor r/min |  |
| Motor kW |  |
| Remarks |  |

END OF SECTION