Section Cover Page

Section 26 00 05 2008-05-01 Basic Electrical Requirements

Use this Section to specify basic electrical requirements, i.e. "general" requirements applicable to most or all electrical work.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Product Options and Substitutions

1.2	Regulatory Requirements

1.3	Submittals

1.4	Operation and Maintenance Data

1.5	Record Drawings

1.6	Coordination

1.7	Source of Supply

1.8	Reference Documents

1.9	Electrical Identification

1.10	Coordination

1.11	Requirements for Existing Occupied Buildings

1.12	Cleaning

2.	Products

Not Used

3.	Execution

Not Used

1.	General

1.1	PRODUCT OPTIONS AND SUBSTITUTIONS

.1	Refer to Division 01 for requirements pertaining to product options and substitutions.

1.2	REGULATORY REQUIREMENTS

.1	Comply with Safety Codes Act and rules and regulations made pursuant thereto, including the Canadian Electrical Code.

.2	Unless otherwise indicated, all references to "Canadian Electrical Code" (CEC) shall mean the current edition of the Canadian Electrical Code, Part I, CSA C22.1, and the variations made thereto by Alberta regulation, which are in force on the date of bid closing for the Contract.

.3	Electrical products shall be tested, certified and labelled in accordance with a certification program accredited by the Standards Council of Canada.  Where a product is not so labelled, provide written approval by the authority having jurisdiction.

.4	Submit to authority having jurisdiction and utility company, necessary number of drawings and specifications for examination and approval prior to commencement of electrical work.  Pay associated fees.

1.3	SUBMITTALS

.1	Submit to Minister, copy of electrical permit obtained from authority having jurisdiction.

.2	If authority having jurisdiction conducts an electrical inspection, submit copy of certificate of acceptance provided by authority having jurisdiction.

.3	Submit shop drawings and, if requested by Minister, samples for the following:

.1	Panelboards.

.2	Luminaires.

.3	Fire alarm panels and components.

.4	Emergency call system and components.

.5	Other items, as requested by Minister.

1.4	OPERATION AND MAINTENANCE DATA

.1	Provide the following for all systems and components for incorporation into Operation & Maintenance Manual specified in Division 01:

.1	Brief description of the systems, wiring diagrams (if applicable), installation and operating instructions and parts list for all serviceable components.

.2	List names, addresses, and telephone numbers, of all suppliers, subcontractors, etc. who supplied and installed the systems.

.3	Copies of all reviewed shop drawings, test reports  inspection certificates, warranties, [fire alarm verification certificate], etc. as applicable.

1.5	RECORD DRAWINGS

.1	Record actual locations of pull boxes, panelboards, luminaires, feeders, electrical equipment and electrical site services.

.2	Record changes to circuit designations.

.3	Record changes in red ink, on a fresh set of blue-line prints.  Blue-line prints to be handed to the Minister upon completion of project

1.6	COORDINATION

.1	Coordinate work specified in Divisions 26 & 27 with work specified in other Divisions.  Ensure that proper arrangements and provisions are made for work specified in Divisions 26 & 27.

1.7	SOURCE OF SUPPLY

.1	Like materials and components shall be by a single manufacturer.

1.8	REFERENCE DOCUMENTS

.1	Comply with standards of following organizations:

.1	Electrical and Electronic Equipment Manufacturers Association of Canada (EEMAC).

.2	Institute of Electrical and Electronic Engineers (IEEE).

1.9	ELECTRICAL IDENTIFICATION

.1	Colour Identification of Equipment:

.1	Electrical equipment shall be prefinished in coded colours as follows:

.1	120/208V or 120/240V Line Voltage Equipment: grey.

.2	Fire Alarm System Equipment: red.

.3	Telephone Cabinets: green.

.4	[            ]:  [     ].

.2	Nameplate Identification:  Identify following equipment with lamicoid nameplates, 3 mm thick, black face, white core, mechanically attached, 20 mm high with 8 mm high letters:

.1	Panelboards:  Indicate voltage and amperage.

.2	Disconnect switches, magnetic motor starters and contactors:  Indicate equipment being controlled.

.3	Wireways.

.4	Line voltage cabinets and enclosures:  Indicate system & voltage.

.5	Low voltage cabinets and enclosures:  Indicate system & voltage.

.6	Pull and junction box covers over 100 mm size.

.3	Panelboard Directories:  Identify loads controlled by each overcurrent protective device in each panelboard, by means of a typewritten panelboard directory.

.4	Colour Identification of Wiring:

.1	Colour coding shall be in accordance with Canadian Electrical Code.

.2	Maintain phase sequence and colour coding throughout each system.

1.10	COORDINATION

.1	Coordinate with other divisions for connection of equipment, for requirements pertaining to electrical connection of equipment supplied and installed under other Divisions.

SPEC NOTE:  Specify in a separate Section, a comprehensive list or schedule of equipment requiring electrical connection and requirements related thereto.

1.11	REQUIREMENTS FOR EXISTING OCCUPIED BUILDINGS

.1	Make changes to the existing system at times arranged by the Minister's representative. Changes to existing systems should not interfere with the operation and use of the existing facilities.

.2	Remove existing conduit and electrical equipment being abandoned.  Blank coverplates on abandoned boxes are not acceptable.  Dispose of removed and surplus conduit, wire, fittings and equipment as directed by the Minister.

.3	Existing conduit and fittings may be reused providing they are free of dents and bruises and are not deformed.  Do not reuse removed existing conductors.

1.12	CLEANING

.1	Do the following prior to Interim Acceptance of the Work, as required to remove all construction dust and debris:

.1	Clean out all cabinets and enclosures with vacuum or compressed air.

.2	Wipe all insulators with clean, dry rags.

.3	Clean all luminaires, with vacuum or clean dry rags.

2.	Products

Not used.

3.	Execution

Not used.

END OF SECTION