Section Cover Page

Section 33 30 10 2018-08-15 Sewer System

Use this Section to specify requirements which apply specifically to sewer system.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Sections

1.3	Reference Documents

1.4	Section Includes

1.5	Detail Drawings

1.6	Inspections by the Province

2.	Products

2.1	Material Schedule

2.2	Bedding Materials

3.	Execution

3.1	Bedding

3.2	Pipe Laying

3.3	Manholes and Catch Basins

3.4	Flushing

.3	Detail Drawings:

33 30 10.01		Precast Manhole

33 30 10.02		Drop Manhole

33 30 10.03		750 mm Catchbasin

33 30 10.04		Manhole Invert on Intersection Less than 90°

33 30 10.05		Sewer Service Connection

33 30 10.06		Sewer Riser

END OF DATA SHEETS

1.	General

1.1	INTENT

.1	Read this section in conjunction with Section 33 05 10 - Piped Utility Systems General Requirements.

1.2	RELATED SECTIONS

.1	Fill Materials:	Section 31 05 13.

.2	Trench Excavating & Backfilling:	Section 31 23 38.

1.3	Reference documents

.1	American Society for Testing and Materials (ASTM):

| .1 | ASTM C76-16 | Standard Specification for Reinforced Concrete Culvert, Storm Drain, and Sewer Pipe. |
| --- | --- | --- |

.2	Canadian Standards Association (CSA):

| .1 | CAN/CSA A257 Series-14 | Standards for Concrete Pipe and Manhole Sections. |
| --- | --- | --- |
| .2 | CSA B182.1-15 | Plastic Drain and Sewer Pipe and Pipe Fittings. |
| .3 | CSA B182.2-15 | PSM Type Polyvinylchloride (PVC) Sewer Pipe and Fittings. |
| .4 | CSA G401-14 | Corrugated Steel Pipe Products. |

1.4		SECTION INCLUDES

.1	This Section includes all requirements for sewer system, including materials, installation of pipes and appurtenances.

1.5	DETAIL DRAWINGS

.1	Following detail drawings are appended hereto and form part of this Section.

33 30 10.01			Precast Manhole

33 30 10.02			Drop Manhole

33 30 10.03			750 mm Catchbasin

33 30 10.04			Manhole Invert on Intersection

Less than 90°

33 30 10.05			Sewer Service Connection

33 30 10.06			Sewer Riser

SPEC NOTE:  Include only those detail drawings applicable to project.  Co-ordinate working drawing details with detail drawings.  Fill in missing dimensions on detail drawings.

1.6	INSPECTION BY The Province

SPEC NOTE:  Delete this Section for projects involving very short lines.

.1	The Province will arrange and pay for a camera inspection after the sewers have been installed and flushed.  Rectify defects detected by this inspection.

.2	Approximately one month before expiry of the warranty period, pipe flushing and a TV inspection will be arranged and paid for by the the Province.  Rectify defects detected by this inspection.

2.	Products

2.1	MATERIALS SCHEDULE

| Material | Standard | Type | Joints |
| --- | --- | --- | --- |
| PVC Pipe | CSA B182.1-96 | SDR [35][28] | [Rubber gasketed |
|  | (100 to 150 mm) |  | bell end] |
|  | CSA B182.2-95 |  |  |
|  | (200 to 675 mm) |  |  |
| Non- | CSA A257.0-M92 | Class 3 | [Rubber gasket to |
| Reinforced | CSA A257.1-M92 | Sulfate | CSA A257.3-M92] [Bell |
| Concrete | (up to 600 mm) | resistant | and spigot] |
| Pipe |  | cement |  |
| Reinforced | CSA A257.0-M92 | [40D][50D][65D] | [Rubber Gasket to |
| Concrete | CSA A257.2-M92 | [100D][140D] | CSA A257.3-M92] [Bell |
| Pipe | (300 mm & over) | Sulfate re- | and spigot] |
|  |  | sistant cement |  |
| Corrugated | CSA-G401-93 | Galvanized | [Welded] |
| Steel |  |  | [Coupled] |
| Precast | ASTM C76-95a | Sulfate resist- | [Rubber gasket |
| Manhole |  | ant cement c/w | to CSA A257.3-M92] |
|  |  | galvanized |  |
|  |  | ladder rungs |  |
| Precast | - | Sulfate resist- | - |
| manhole base, |  | ant cement |  |
| slab top |  |  |  |
| Catch Basin | As detailed |  |  |
| Manhole | Standard |  |  |
| cover | cast iron |  |  |

2.2	BEDDING MATERIALS

.1	Granular Material:  [Sand] [   ] mm Crushed Gravel] as specified in Section 31 05 13.

3.	Execution

3.1	BEDDING

.1	Provide Class [A] [B] [C] bedding as indicated on detail drawing appended to Section 33 05 10.

3.2	PIPE LAYING

.1	Lay pipes with bell-end upgrade.

.2	Provide and utilize "laser" type instrument to control line and grade for grades less than 0.5%.  For steeper grades, use approved and accepted method of establishing grades.

.3	Ensure that the installed lines have a smooth and uniform invert.

3.3	MANHOLES AND CATCH BASINS

.1	Set precast base of [manholes] [and catch basins] to proper grade and location specified.

AND/OR

.2	Construct poured-in-place concrete base for [manholes] [and catch basins] to proper grade and location specified.	Imbed [manholes] [and catch basins] into soft concrete of base as soon after pouring as possible.  Ensure correct grade and location.

.4	Safety rungs shall be installed in all precast manhole sections, including the neck and in the cast-in-place section to form a continuous ladder, with rungs equally spaced at a maximum of 410 mm, from within 300 mm below the cover, to within 600 mm of the base or benching. The rungs shall be cast firmly in place or secured with a suitable mechanical anchorage to prevent pullout and maintain water tightness

.5	Set cast iron covers to finished grade.

.6	Form smooth channels across manhole base.  Set inverts of channels to invert elevations specified for pipe.  Ensure channels are as wide and deep as diameter of outlet pipe.

.7	Cut out openings for pipe in [manholes] [and catch basins] 150 mm maximum larger than pipe diameter.  Place cement grout in voids between pipe and manhole.

.8	Place cement grout in barrel joints [during] [after] erection or use preformed rubber gaskets.

.9	Set base of catch basins and catch basin manholes [450] [600] mm below outlet invert.

.10	Install manholes to provide minimum 500 mm and maximum 750 mm long neck.

3.4	FLUSHING

.1	Flush out new sewer system to ensure free running pipes.  Supply all equipment and water required.

.2	Remove dirt and debris from [manholes] [and catch basins].

END OF SECTION